## Overall
Overall Summary of Analysis Data (Round-01 of 2024)
Summary of FSTP Effluent analysis by DPHE FSL | Parameters
| pH | Temp (Degree C) | BOD (mg/l) | COD (mg/l) | Total Nitrogen (mg/l) | Nitrate (mg/l) | Phosphate (mg/l) | Total Suspended Solids (mg/l) | Oil & Grease (mg/l) | Total Coliforms (cfu/100 ml) | E. Coli (cfu/100 ml)
Minimum | 6.15 | 22.8 | 39 | 92.2 | 50.3 | 1.86 | 0.12 | 10 |  | 0 | 0
Maximum | 9.25 | 34.5 | 1305 | 2089 | 1408 | 352 | 141.2 | 1400 |  | 159700 | 150700
Average | 8.331 | 28.4623 | 227.1494 | 792.7091 | 569.7532 | 36.9913 | 40.6605 | 179.457 |  | 18895.4545 | 6985.7143
Median | 8.35 | 28.65 | 202 | 743.5 | 526.5 | 22.05 | 37.4 | 136.665 |  | 7300 | 300
Govt Std (DoE 2023) | 6 to 9 | 30 | 30 | 125 | N/A | 50 | 15 | 100 | 10 | 1000 | N/A
No of FSTPs above limit | 10 | 45 | 154 | 152 |  | 21 | 114 | 83 | 154 | 116
% of FSTPs above limit | 6.494% | 29.22% | 100% | 98.7% |  | 13.64% | 74.03% | 53.9% | 100% | 75.32%
FSTP visited | 194
Operational FSTPs, with samples analyzed | 170
FSTPs under maintenance, not analyzed | 15
Functional but not operational | 7
Technology Upgradation ongoing | 2

## Non Functional FSTPs
Non Functional FSTP list
S/N | Organization | WASH AFA | FSTP ID (DPHE) | FSTP ID (Organization) | Camp ID | Block | Sub Block | FSTP Type | Status
1 | NGOF | UNHCR | FSTP-KRC-01 | NGOF-KRC-ABR-01 | KRC | A | A-3 | ABR | Functional but non-operational
2 | NGOF | UNHCR | FSTP-KRC-02 | NGOF-KRC-ABR-02 | KRC | D |  | ABR | Functional but non-operational
3 | NGOF | UNHCR | FSTP-KRC-03 | NGOF-KRC-ABR-03 | KRC | F |  | ABR | Functional but non-operational
4 | NGOF | UNHCR | FSTP-KRC-04 | NGOF-KRC-ASTT-01 | KRC | E |  | ASTT | Functional but non-operational
5 | NGOF | UNHCR | FSTP-26-01 | NGOF-C26-LSP-01 | 26 | E | E-2 | LSP | Functional but non-operational
6 | NGOF | UNHCR | FSTP-NRC-01 | NGOF-NRC-ABR-01 | NRC | C |  | ABR | Functional but non-operational
7 | Anando | IOM | FSTP-25-03 | IOM-DEWATS-2023-01-C25-001 | 25 | A | A-4 | DEWATS | Functional but non-operational
8 | DSK | IOM | FSTP-18-11 | IOM-DEWATS-2023-06-C18-001 | 18 | C | C-5 (K-10) | DEWATS | Technology Upgradation ongoing
9 | DSK | IOM | FSTP-18-12 | IOM-DEWATS-2023-06-C18-002 | 18 | A | A-1 (H-64) | DEWATS | Technology Upgradation ongoing
10 | SHED | IOM | FSTP-20-17 | IOM-DLT-012-KSR-30 | 20 Ext | S-2 | B-2 | SSU | Under maintainance
11 | SHED | IOM | FSTP-20-21 | IOM-DLT-2018-10-11 | 20 Ext | S-4 | B-5 | SSU | Under maintainance
12 | SHED | IOM | FSTP-20-10 | IOM-DLT-007 (KSR-25) | 20 Ext | S-3 | B-2 | SSU | Under maintainance
13 | NGOF | UNICEF | FSTP-07-07 | WVI UFF-05 | 7 | C | C-5 | UFF | Under maintainance
14 | NGOF | IOM | FSTP-09-03 | ABR-01 | 9 | F | C-9 | ABR | Under maintainance
15 | BRAC | IOM | FSTP-10-08 | LSP-F-40-01 | 10 | E | F-40 | LSP | Under maintainance
16 | Caritas | UNHCR | FSTP-17-01 | NGOF-C17-ABR-01 | 17 | C | C-101 | ABR | Under maintainance
17 | Caritas | UNHCR | FSTP-17-02 | NGOF-C17-ABR-02 | 17 | C | C-76 | ABR | Under maintainance
18 | DSK | IOM | FSTP-18-02 | IOM-DLT-2018-07-C18-002 | 18 | A | A-1 (H-66) | SSU | Under maintainance
19 | BRAC | UNHCR | FSTP-21-03 | C-21-LSP-Chakmarkul | 21 | E | E-1 | LSP | Under maintainance
20 | BRAC | UNICEF | FSTP-14-01 | C-14-A-A4-FSM-01 | 14 | A | A4 | ABR | Under maintainance
21 | WVI | IOM | FSTP-13-10 | WSP-01 | 13 | A | A-6 | WSP | Under maintainance
22 | BDRCS | IOM | FSTP-13-03 | PA-FSTP-2 | 13 | G | G-3 | UFF | Under maintainance
23 | WVI | IOM | FSTP-13-04 | WSP-03 | 13 | G | G-3 | WSP | Under maintainance
24 | ICDDRB Hospital | - | FSTP-H-04 | ICDDRB Hospital FSTP | Host Community |  |  | ABR | Under maintainance

## Analysis Data (Round 08-2025)
S/N | Organization | Sample ID | Sample Collection | Camp ID | WASH AFA | FSTP ID (By DPHE) | FSTP ID (Organization) | Block | Sub Block | Technology Type | Capacity (m3/week) | Latitude | Longitude | Sample Type | pH | Temperature (Degree C) | TN (mg/l) | Nitrate (mg/l) | Phosphate (mg/l) | BOD (mg/l) | COD (mg/l) | E.Coli (cfu/100 ml) | Total Coliform (Cfu/100 ml) | TSS (mg/l) | TS (%) | Oil & Grease (mg/l) | Conductivity (µS/cm) | Incharge of FSTP | Contact Number | Alternative Number | Remarks
1 | NGOF | DPHE-FSL-S-1269 | 18/02/2025 | 7 | UNICEF | FSTP-07-03 | UFF-02 | B | B5 | UFF | 15 | 21.2039 | 92.1677 | Effluent | 8.34 | 25.4 | 466 | 30 | 82.8 | 260 | 906 | 0 | 0 | 171.42 | 38.84% | 612 | 6500
2 | NGOF | DPHE-FSL-S-1270 | 18/02/2025 | 7 | UNICEF | FSTP-07-01 | UFF-05 | A | A7 | UFF | 30 | 21.2056 | 92.1697 | Effluent | 8.28 | 26.3 | 601 | 44.8 | 50.8 | 380 | 1103 | 0 | 0 | 266.66 | 27.12% | 496 | 8970
3 | NGOF | DPHE-FSL-S-1271 | 18/02/2025 | 7 | UNICEF | FSTP-07-02 | UFF-01 | B | B1 | UFF | 15 | 21.2056 | 92.1697 | Effluent | 7.94 | 29.4 | 1040 | 39.3 | 101.2 | 620 | 1777 | 0 | 0 | 333.33 | 41.27% | 928 | 8250
4 | NGOF | DPHE-FSL-S-1272 | 18/02/2025 | 7 | UNICEF | FSTP-07-07 | UFF-09 | C | C-1 | UFF | 15 | 21.2045 | 92.1663 | Effluent | 8.69 | 26.3 | 640 | 105 | 51.6 | 280 | 890 | 100 | 12800 | 37.04 | 64.27% | 1776 | 6040
5 | NGOF | DPHE-FSL-S-1273 | 18/02/2025 | 7 | UNICEF | FSTP-07-08 | WVI WSP-03 | C | C1 | WSP | 15 | 21.2036 | 92.1656 | Effluent | 8.75 | 26.9 | 691 | 58.9 | 31.2 | 312 | 912 | 1100 | 7100 | 266.66 | 51.75% | 218 | 4270
6 | NGOF | DPHE-FSL-S-1274 | 23/02/2025 | 26 | UNHCR | FSTP-26-03 | NGOF-C26-ADS-01 | I | I-5 | ADS | 25 | 20.9661 | 92.2453 | Effluent | 8.27 | 31.8 | 401 | 350 | 18.98 | 130 | 380 | 1000 | 47000 | 57.14 | 2.58% | 432 | 4220
7 | NGOF | DPHE-FSL-S-1275 | 23/02/2025 | 26 | UNHCR | FSTP-26-04 | FSTP-03 (Mega FSTP-03) | G | G1 | Biological Process | 350 | 21.2096 | 92.2528 | Effluent | 7.77 | 30.4 | 590 | 257 | 28.2 | 55 | 490 | 900 | 50900 | 40 | 2.83% | 444 | 6170
8 | NGOF | DPHE-FSL-S-1276 | 23/02/2025 | NRC | UNHCR | FSTP-NRC-01 | NGOF-NRC- ABR-01 | C |  | ABR | 10 | 20.9529 | 92.2513 | Effluent | 8.86 | 27.1 | 1198 | 25.7 | 50.2 | 155 | 789 | 600 | 8900 | 250 | 2.66% | 296 | 4920
9 | TDH | DPHE-FSL-S-1277 | 23/02/2025 | 27 | UNHCR | FSTP-27-03 | C-27-TDH-LSP | A |  | LSP | 25 | 20.9474 | 92.2606 | Effluent | 8.98 | 27.2 | 1388 | 28.9 | 9.96 | 197 | 971 | 0 | 1500 | 250 | 1.94% | 242 | 5650
10 | NGOF | DPHE-FSL-S-1278 | 23/02/2025 | 27 | UNHCR | FSTP-27-01 | NGOF-C-27-ABR-01 | C | C-10 | ABR | 50 | 20.9031 | 92.262 | Effluent | 8.77 | 31.1 | 396 | 19.4 | 6.8 | 248 | 1434 | 0 | 0 | 200 | 2.21% | 492 | 5890
11 | Teknaf Municipality | DPHE-FSL-S-1279 | 23/02/2025 | Host community |  | FSTP-H-03 | Teknaf Municipality |  |  | Anarobic Legone | 140 | 20.853 | 92.3051 | Effluent | 8.35 | 27.6 | 179 | 119 | 3.06 | 56 | 282 | 3100 | 41100 | 10 | 0.11% | 324 | 3070
12 | NGOF | DPHE-FSL-S-1280 | 24/02/2025 | 7 | UNICEF | FSTP-07-06 | WSP-02 | C | C-2 | WSP | 15 | 21.2036 | 92.1655 | Effluent | 8.74 | 26.1 | 164 | 57.8 | 4.96 | 61 | 141 | 0 | 300 | 20 | 0.5% | 144 | 1600
13 | NGOF | DPHE-FSL-S-1281 | 24/02/2025 | 7 | UNICEF | FSTP-07-13 | UFF-07 | E | E2 | UFF | 30 | 21.2019 | 92.1639 | Effluent | 8.46 | 25 | 205 | 24.2 | 3.6 | 39 | 189 | 3400 | 35000 | 10 | 0.34% | 120 | 2090
14 | NGOF | DPHE-FSL-S-1282 | 24/02/2025 | 7 | UNICEF | FSTP-07-12 | ABR-01 | E | E-6 | ABR | 45 | 21.2017 | 92.1625 | Effluent | 8.68 | 24.3 | 353.3 | 29.3 | 62.6 | 265 | 1004 | 200 | 2600 | 66.66 | 1.93% | 104 | 6670
15 | NGOF | DPHE-FSL-S-1283 | 24/02/2025 | 7 | UNICEF | FSTP-07-15 | ABR-04 | G | G-6 | ABR | 15 | 21.2017 | 92.1612 | Effluent | 8.6 | 25.8 | 385 | 41 | 25.6 | 178 | 714 | 100 | 1100 | 100 | 1.63% | 188 | 6200
16 | NGOF | DPHE-FSL-S-1284 | 24/02/2025 | 7 | UNICEF | FSTP-07-14 | ABR-04 | G | G-5 | ABR | 15 | 21.2008 | 92.1597 | Effluent | 8.26 | 25.6 | 417 | 26.3 | 103 | 370 | 1126 | 1000 | 1500 | 300 | 1.71% | 120 | 7710
17 | NGOF | DPHE-FSL-S-1285 | 24/02/2025 | 7 | UNICEF | FSTP-07-11 | UFF-06 | E | E-2 | UFF | 20 | 21.2033 | 92.1618 | Effluent | 8.14 | 26.8 | 308.7 | 30.4 | 112.8 | 480 | 1343 | 0 | 500 | 400 | 2.71% | 152 | 7910
18 | NGOF | DPHE-FSL-S-1286 | 24/02/2025 | 7 | UNICEF | FSTP-07-04 | UFF-04 | D | D-4 | UFF | 15 | 21.2087 | 92.1545 | Effluent | 8.96 | 25.6 | 443.1 | 29.6 | 39.4 | 448 | 1226 | 1000 | 2100 | 266.66 | 1.83% | 600 | 3260
19 | NGOF | DPHE-FSL-S-1287 | 24/02/2025 | 7 | UNICEF | FSTP-07-05 | ABR-03 | D | D-6 | ABR | 15 | 21.2026 | 92.1651 | Effluent | 8.74 | 26.1 | 305.1 | 25.7 | 37.2 | 79 | 410 | 300 | 12700 | 20 | 1.11% | 112 | 2210
20 | MSF-OCA | DPHE-FSL-S-1288 | 24/02/2025 | Host community (Thaing Khali) | MSF | FSTP-H-02 | FSTP-01 |  |  | Biological Process | 50 | 21.1836 | 92.1564 | Effluent | 8.8 | 27.8 | 208.8 | 19.8 | 51.6 | 275 | 552 | 300 | 22300 | 166.66 | 0.98% | 120 | 1590
21 | BRAC | DPHE-FSL-S-1289 | 2025-02-03 | Kutupalong | UNHCR | FSTP-H-01 | FSTP-02 (Mega FSTP) | E | A-14 | Biological Process | 455 | 21.2102 | 92.1698 | Effluent | 8.45 | 28.4 | 195 | 352 | 40 | 91 | 395 | 100 | 31300 | 140 | 1.84% | 196 | 8460
22 | BRAC | DPHE-FSL-S-1290 | 25/02/25 | 1E | UNHCR | FSTP-H-01-01 | 1-E ABR | B | B-12 | ABR | 15 | 21.2194 | 92.1512 | Effluent | 7.97 | 25.1 | 848 | 25.1 | 95 | 187 | 479 | 0 | 5700 | 200 | 1.22% | 720 | 3190
23 | BRAC | DPHE-FSL-S-1291 | 25/02/2025 | 1W | UNHCR | FSTP-01-02 | 1W ABR | E | E-2 | ABR | 50 | 21.0613 | 92.1538 | Effluent | 8.53 | 25.2 | 1120 | 29.4 | 96.2 | 480 | 1116 | 0 | 0 | 150 | 2.4% | 760 | 4380
24 | WB | DPHE-FSL-S-1292 | 25/02/2025 | 2W | DPHE | FSTP-02-01 | Package(WB-09) | B | B-6 | ABR | 64 | 21.2068 | 92.1598 | Effluent | 8.61 | 28.6 | 314 | 338 | 8.52 | 384 | 493 | 6700 | 36700 | 100 | 2.25% | 840 | 3260
25 | DPHE | DPHE-FSL-S-1293 | 25/02/2025 | 12 | WB | FSTP-12-05 | WD-09, ABR | G-13 | C-3 | ABR | 36 | 21.1815 | 92.148 | Effluent | 9 | 29.5 | 338 | 178 | 26.2 | 365 | 677 | 0 | 6500 | 30 | 1.82% | 144 | 1560
26 | DSK | DPHE-FSL-S-1294 | 25/02/2025 | 12 | IOM | FSTP-12-03 | IOM-DEWATS-2023-01,C-12-003 | C | J-12 | DEWATS | 18.6 | 21.1824 | 92.1481 | Effluent | 7.91 | 27.2 | 188 | 49.7 | 1.5 | 76 | 149 | 0 | 1900 | 100 | 1.81% | 1000 | 1430
27 | DSK | DPHE-FSL-S-1295 | 25/02/2025 | 12 | IOM | FSTP-12-04 | IOM-DEWATS-2023-02,C-12-004 | C | J-12 | DEWATS | 18.6 | 21.1831 | 92.1483 | Effluent | 7.92 | 27.3 | 788 | 27 | 32.4 | 306 | 497 | 0 | 0 | 60 | 1.24% | 840 | 3100
28 | DSK | DPHE-FSL-S-1296 | 25/02/2025 | 12 | IOM | FSTP-12-01 | IOM-DEWATS-2020-09,C-12-001 | A | G-9 | DEWATS | 18.6 | 21.1788 | 92.1539 | Effluent | 8.24 | 27.4 | 125.2 | 65.3 | 19.46 | 45 | 172 | 0 | 100 | 200 | 1.02% | 80 | 900
29 | DSK | DPHE-FSL-S-1297 | 25/02/2025 | 12 | IOM | FSTP-12-02 | IOM-DEWATS-2020-09,C-12-002 | A | G-9 | DEWATS | 18.6 | 21.1787 | 92.154 | Effluent | 8.71 | 24.7 | 772 | 32.4 | 42.8 | 288 | 473 | 100 | 100 | 150 | 1.03% | 120 | 2870
30 | DSK | DPHE-FSL-S-1298 | 25/02/2025 | 5 | UNHCR | FSTP-05-02 | NGOF-C-5-ABR-02 | E | E-3 | ABR | 50 | 21.2013 | 92.15 | Effluent | 9.11 | 27 | 254 | 41.7 | 27.8 | 305 | 823 | 700 | 32700 | 140 | 2.25% | 296 | 1040
31 | DPHE | DPHE-FSL-S-1299 | 25/02/2025 | 4 Ext | ADB | FSTP-04-03 | Omni-1 | B | B-2 | Omni Processor | 180 | 21.2096 | 92.135 | Effluent | 7.48 | 28.2 | 378 | 23.2 | 26.6 | 115 | 308 | 2400 | 44400 | 166.66 | 0.61% | 920 | 900
32 | NGOF | DPHE-FSL-S-1300 | 2025-02-03 | 9 | IOM | FSTP-09-02 | IOM-DLT-2017-06-BMS-001 | F | C-9 | SSU | 6 | 21.1894 | 92.1603 | Effluent | 8.71 | 23.1 | 645 | 30.9 | 63 | 456 | 1261 | 0 | 4300 | 250 | 2.22% | 1120 | 3280
33 | NGOF | DPHE-FSL-S-1301 | 2025-02-03 | 9 | IOM | FSTP-09-03 | ABR-01 | F | C-9 | ABR | 30 | 21.1894 | 92.1603 | Effluent | 8.27 | 24.9 | 852 | 53.6 | 110.6 | 285 | 2089 | 2100 | 23600 | 1000 | 3.23% | 440 | 3230
34 | NGOF | DPHE-FSL-S-1302 | 2025-02-03 | 9 | IOM | FSTP-09-06 | IOM-DLT-2017-06-BMS-002 | A | B-1 | SSU | 6 | 21.1921 | 92.1604 | Effluent | 8.46 | 24.7 | 861 | 35.8 | 90 | 336 | 1379 | 0 | 200 | 352.94 | 0.14% | 440 | 3770
35 | NGOF | DPHE-FSL-S-1303 | 2025-02-03 | 9 | IOM | FSTP-09-07 | IOM-DEWATS-2019-10-C09-001 | A | B-2 | DEWATS | 15 | 21.1924 | 92.1596 | Effluent | 8 | 29.1 | 281 | 40.5 | 127 | 317 | 1250 | 0 | 100 | 266.66 | 0.32% | 200 | 5240
36 | NGOF | DPHE-FSL-S-1304 | 2025-02-03 | 9 | IOM | FSTP-09-08 | IOM-DEWATS-2021-07-C09-002 | B | I-2 | DEWATS | 18 | 21.1926 | 92.1584 | Effluent | 7.76 | 31.8 | 1260 | 37.6 | 141.2 | 247 | 1306 | 0 | 200 | 250 | 3.33% | 360 | 5290
37 | NGOF | DPHE-FSL-S-1305 | 2025-02-03 | 9 | IOM | FSTP-09-09 | IOM-DLT-2017-06-BMS-003 | C | H-20 | SSU | 6 | 21.1922 | 92.1572 | Effluent | 8.81 | 26.6 | 690 | 12.67 | 21.54 | 235 | 1252 | 0 | 40600 | 100 | 5.12% | 120 | 3050
38 | NGOF | DPHE-FSL-S-1306 | 2025-02-03 | 6 | UNICEF | FSTP-06-02 | ABR-FSM-02 | B | B-12 | ABR | 90 | 21.2043 | 92.1585 | Effluent | 8.47 | 27.2 | 1020 | 26 | 106 | 270 | 1144 | 700 | 1500 | 50 | 0.49% | 40 | 4080
39 | NGOF | DPHE-FSL-S-1307 | 2025-02-03 | 6 | UNICEF | FSTP-06-01 | ABR-FSM-01 | D | D-2 | ABR | 90 | 21.2018 | 92.1582 | Effluent | 8.74 | 26.9 | 1010 | 63.7 | 107.2 | 183 | 1028 | 0 | 200 | 233.33 | 3.08% | 360 | 4020
40 | NGOF | DPHE-FSL-S-1308 | 2025-02-03 | 6 | UNICEF | FSTP-06-04 | ABR-FSM-03 | C | C-3 | ABR | 90 | 21.2037 | 92.1561 | Effluent | 9.07 | 26.6 | 174 | 23.5 | 67 | 151 | 1113 | 2100 | 9600 | 200 | 4.47% | 240 | 3630
41 | NGOF | DPHE-FSL-S-1309 | 2025-02-03 | 6 | UNICEF | FSTP-06-03 | ABR-FSM-04 | A | A-2 | ABR | 90 | 21.2064 | 92.1563 | Effluent | 8.74 | 28 | 858 | 60.8 | 89.6 | 110 | 1066 | 1500 | 5600 | 200 | 2.51% | 40 | 3570
42 | NGOF | DPHE-FSL-S-1310 | 2025-02-03 | 4 Ext | UNHCR | FSTP-04-01 | FSTP-01 |  |  | Anarobic Legone | 700 | 21.2129 | 92.1391 | Effluent | 8.69 | 26.5 | 584 | 182 | 23.4 | 126 | 545 | 1100 | 27500 | 50 | 5.5% | 720 | 2210
43 | WVI | DPHE-FSL-S-1311 | 2025-03-03 | 8E | UNICEF | FSTP-08-02 | ABR-4 | B | B-60 | ABR | 50 | 21.1965 | 92.1614 | Effluent | 8.69 | 26.3 | 195 | 11.4 | 3.92 | 396 | 748 | 200 | 1100 | 250 | 2.05% | 352 | 3400
44 | WVI | DPHE-FSL-S-1312 | 2025-03-03 | 8E | UNICEF | FSTP-08-03 | UFF-03 | B | B-42 | UFF | 25 | 21.1998 | 92.1602 | Effluent | 8.1 | 27.2 | 302 | 29.8 | 15.28 | 119 | 1442 | 0 | 3900 | 200 | 1.99% | 640 | 3400
45 | WVI | DPHE-FSL-S-1313 | 2025-03-03 | 8E | UNICEF | FSTP-08-05 | WSP-02 | E | B-86 | WSP | 25 | 21.1985 | 92.1643 | Effluent | 8.53 | 25.5 | 350.7 | 24.5 | 9.02 | 106 | 258 | 200 | 19500 | 40 | 1.2% | 200 | 1250
46 | WVI | DPHE-FSL-S-1314 | 2025-03-03 | 8E | UNICEF | FSTP-08-01 | C-8E-C-B-65-01 | C | B-65 | WSP | 25 | 21.1948 | 92.1633 | Effluent | 8.05 | 25.9 | 401 | 17 | 24.6 | 226 | 1090 | 200 | 1100 | 200 | 2.21% | 520 | 4450
47 | WVI | DPHE-FSL-S-1315 | 2025-03-03 | 8E | UNICEF | FSTP-08-04 | ABR-08 | F | B-37 | ABR | 30 | 21.1975 | 92.1626 | Effluent | 8.19 | 29.3 | 101 | 24 | 9.3 | 301 | 856 | 900 | 7500 | 150 | 2.03% | 1080 | 3910
48 | WVI | DPHE-FSL-S-1316 | 2025-03-03 | 8E | UNICEF | FSTP-08-07 | UFF-06 | F | B-53 | UFF | 15 | 21.1975 | 92.1656 | Effluent | 8.84 | 26.8 | 365 | 15.6 | 0.22 | 212 | 881 | 0 | 11600 | 550 | 1.82% | 640 | 2630
49 | WVI | DPHE-FSL-S-1317 | 2025-03-03 | 8E | UNICEF | FSTP-08-06 | ABR-07 | D | B-70 | ABR | 50 | 21.1984 | 92.1668 | Effluent | 8.49 | 24.9 | 321 | 14.6 | 1.6 | 146 | 801 | 400 | 11300 | 100 | 1.4% | 40 | 2270
50 | BRAC | DPHE-FSL-S-1318 | 2025-04-03 | 10 | IOM | FSTP-10-07 | DEWATS-01 | E | F-40 | DEWATS | 18 | 21.1877 | 92.1517 | Effluent | 8.17 | 25.9 | 250.1 | 12 | 0.432 | 102 | 496 | 0 | 1100 | 50 | 2.43% | 400 | 3710
51 | BRAC | DPHE-FSL-S-1319 | 2025-04-03 | 10 | IOM | FSTP-10-05 | DEWATS-05 | F | G-6 | DEWATS | 12 | 21.1871 | 92.1576 | Effluent | 7.8 | 25.8 | 211.5 | 20.6 | 13.41 | 42 | 161 | 0 | 700 | 20 | 2.39% | 160 | 1810
52 | BRAC | DPHE-FSL-S-1320 | 2025-04-03 | 10 | IOM | FSTP-10-06 | IOM-23-01-C-03 | C | G-41 | DEWATS | 12 | 21.19 | 92.1546 | Effluent | 7.83 | 27.5 | 241.6 | 33.5 | 15.78 | 311 | 881 | 300 | 1700 | 250 | 0.8% | 840 | 3430
53 | BGS | DPHE-FSL-S-1321 | 2025-04-03 | 10 | IOM | FSTP-10-01 | L-004 | B | H-37 | LSP | 19 | 21.1944 | 92.1531 | Effluent | 9.25 | 28 | 381.9 | 18 | 11.32 | 406 | 1219 | 1600 | 4700 | 100 | 1.8% | 2320 | 3120
54 | WVI | DPHE-FSL-S-1322 | 2025-04-03 | 10 | IOM | FSTP-10-03 | D-001 | A | H-25 | DEWATS | 12 | 21.1927 | 92.1534 | Effluent | 8.19 | 29.3 | 260 | 20.3 | 1.22 | 339 | 1284 | 900 | 1700 | 1400 | 2.41% | 2000 | 4520
55 | WVI | DPHE-FSL-S-1323 | 2025-04-03 | 10 | IOM | FSTP-10-02 | IOM-DE-23-02-04 | A | A-27 | DEWATS | 12 | 21.1914 | 92.1562 | Effluent | 7.95 | 27.4 | 245 | 32.9 | 21.2 | 196 | 677 | 0 | 2300 | 50 | 1.6% | 240 | 3820
56 | DPHE/ ADB | DPHE-FSL-S-1324 | 2025-04-03 | 13 | ADB | FSTP-13-11 | W9-B | F | F-5 | Biological Process | 50 | 21.1832 | 92.1371 | Effluent | 8.84 | 31.4 | 165 | 29.8 | 6.2 | 216 | 723 | 700 | 3700 | 155.55 | 2.43% | 600 | 2300
57 | VERC | DPHE-FSL-S-1325 | 2025-09-03 | 8W | UNICEF | FSTP-08-11 | FSM-01 | B | A-16 | ABR | 60 | 21.1957 | 92.1577 | Effluent | 8.18 | 25.8 | 279 | 42.1 | 28.6 | 119 | 295 | 8700 | 48700 | 20 | 0.86% | 720 | 1260
58 | VERC | DPHE-FSL-S-1326 | 2025-09-03 | 8W | UNICEF | FSTP-08-13 | FSM-01 | D | A-39 | ABR | 30 | 21.199 | 92.1558 | Effluent | 8.2 | 25.6 | 139 | 3.26 | 15.2 | 51 | 238 | 150700 | 159700 | 80 | 0.78% | 280 | 680
59 | VERC | DPHE-FSL-S-1327 | 2025-09-03 | 8W | UNICEF | FSTP-08-14 | FSM-01 | D | I-20 | UFF | 10 | 21.1981 | 92.155 | Effluent | 8.07 | 25.6 | 293 | 56.8 | 23.6 | 65 | 427 | 65000 | 66000 | 177.77 | 1.1% | 160 | 1270
60 | VERC | DPHE-FSL-S-1328 | 2025-09-03 | 8W | UNICEF | FSTP-08-20 | FSM-01 | F | A-65 | ABR | 60 | 21.1967 | 92.1521 | Effluent | 7.98 | 24.1 | 203 | 34.9 | 9.31 | 76 | 227 | 1400 | 51400 | 80 | 1.48% | 1400 | 1160
61 | VERC | DPHE-FSL-S-1329 | 2025-09-03 | 8W | UNICEF | FSTP-08-09 | FSM-01 | A | A-19 | UFF | 15 | 21.1978 | 92.1601 | Effluent | 8.35 | 22.8 | 488 | 47.8 | 46 | 262 | 789 | 76800 | 78100 | 166.66 | 3.26% | 640 | 2490
62 | VERC | DPHE-FSL-S-1330 | 2025-09-03 | 8W | UNICEF | FSTP-08-10 | FSM-01 | A | A-28 | UFF | 15 | 21.1986 | 92.1584 | Effluent | 7.35 | 24.4 | 244 | 4.42 | 47.1 | 114 | 303 | 120300 | 127500 | 20 | 1.42% | 160 | 1180
63 | VERC | DPHE-FSL-S-1331 | 2025-10-03 | 8W | UNICEF | FSTP-08-15 | FSM-01 | E | A-49 | UFF | 15 | 21.1992 | 92.154 | Effluent | 7.92 | 26.4 | 109 | 13.5 | 2.5 | 90 | 176 | 59200 | 67900 | 20 | 1.21% | 200 | 860
64 | VERC | DPHE-FSL-S-1332 | 2025-10-03 | 8W | UNICEF | FSTP-08-20 | FSM-01 | F | A-61 | UFF | 10 | 21.1954 | 92.1537 | Effluent | 8.77 | 25.9 | 916 | 30.4 | 49 | 226 | 1124 | 0 | 0 | 300 | 3.67% | 40 | 3650
65 | VERC | DPHE-FSL-S-1333 | 2025-10-03 | 8W | UNICEF | FSTP-08-16 | FSM-01 | E | A-66 | WSP | 10 | 21.1984 | 92.1509 | Effluent | 7.42 | 27.7 | 50.3 | 5.83 | 1.33 | 44 | 120 | 100 | 3300 | 10 | 0.79% | 240 | 260
66 | VERC | DPHE-FSL-S-1334 | 2025-10-03 | 8W | UNICEF | FSTP-08-19 | FSM-01 | E | A-55 | WSP | 10 | 21.2004 | 92.1518 | Effluent | 7.92 | 27.9 | 164 | 41.5 | 0.12 | 68 | 140 | 4500 | 18900 | 10 | 7.02% | 40 | 320
67 | ACF | DPHE-FSL-S-1335 | 2025-11-03 | 11 | IOM | FSTP-11-05 | DEWATS-02 | A | A-3 | DEWATS | 18 | 21.1834 | 92.1582 | Effluent | 7.95 | 26.7 | 669 | 27.2 | 51.1 | 217 | 724 | 1000 | 51500 | 160 | 4.46% | 80 | 4510
68 | ACF | DPHE-FSL-S-1336 | 2025-11-03 | 11 | IOM | FSTP-11-06 | DEWATS-03 | D | D-7 | DEWATS | 10 | 21.1856 | 92.1566 | Effluent | 8.27 | 27.2 | 838 | 13.5 | 46.4 | 111 | 508 | 5600 | 9700 | 20 | 3.22% | 120 | 3530
69 | ACF | DPHE-FSL-S-1337 | 2025-11-03 | 11 | IOM | FSTP-11-02 | DEWATS-04 | A | A-14 | DEWATS | 15 | 21.1827 | 92.1552 | Effluent | 8.86 | 24.8 | 546 | 55.3 | 55.3 | 135 | 305 | 0 | 200 | 20 | 0.59% | 280 | 2540
70 | ACF | DPHE-FSL-S-1338 | 2025-11-03 | 11 | IOM | FSTP-11-04 | DEWATS-01 | A | A-2 | DEWATS | 18 | 21.1821 | 92.1573 | Effluent | 7.37 | 26 | 843 | 17.4 | 52.6 | 240 | 620 | 900 | 78600 | 120 | 0.4% | 240 | 3820
71 | NRC | DPHE-FSL-S-1339 | 2025-11-03 | 19 | IOM | FSTP-19-02 | IOM-DEWATS-2022-11-C-19-001 | A | A-1 | DEWATS | 15 | 21.1853 | 92.1407 | Effluent | 8.65 | 29.5 | 509 | 21.5 | 61.9 | 253 | 593 | 0 | 2900 | 100 | 2.62% | 2400 | 2050
72 | NRC | DPHE-FSL-S-1340 | 2025-11-03 | 19 | IOM | FSTP-19-03 | IOM-DEWATS-2022-11-C-19-002 | A | A-1 | DEWATS | 15 | 21.1853 | 92.1406 | Effluent | 6.32 | 28.1 | 920 | 18.9 | 133 | 230 | 623 | 200 | 38600 | 10 | 3.2% | 520 | 2020
73 | BDRCS | DPHE-FSL-S-1341 | 2025-11-03 | 19 | IOM | FSTP-19-01 | BDRCS-FSTP-C19-01 | D | D-13 | ABR | 75 | 21.1806 | 92.1475 | Effluent | 8.36 | 28.5 | 725 | 19.9 | 55.4 | 272 | 726 | 0 | 2800 | 160 | 3.03% | 1840 | 1630
74 | DSK | DPHE-FSL-S-1342 | 2025-11-03 | 5 | UNHCR | FSTP-05-03 | NGOF-C-5-ABR-01 | E | E-7 | ABR | 50 | 21.1992 | 92.148 | Effluent | 6.15 | 34.2 | 462 | 11.6 | 3 | 201 | 291 | 1700 | 39500 | 50 | 12.05% | 120 | 4340
75 | BDRCS | DPHE-FSL-S-1343 | 16/03/2025 | 18 | IOM | FSTP-18-01 | FSM-C18-2 | M | M-19 | ABR | 75 | 21.1878 | 92.1441 | Effluent | 7.81 | 26.8 | 466 | 17.8 | 33.2 | 179 | 691 | 100 | 100 | 40 | 3.19% | 240 | 1960
76 | DSK | DPHE-FSL-S-1344 | 16/03/2025 | 18 | IOM | FSTP-18-05 | DEWATS-01 | C | K-9 | DEWATS | 18 | 21.1876 | 92.1516 | Effluent | 7.68 | 28.9 | 710 | 77.2 | 3.44 | 204 | 628 | 0 | 0 | 30 | 1.68% | 320 | 2200
77 | DSK | DPHE-FSL-S-1345 | 16/03/2025 | 18 | IOM | FSTP-18-12 | IOM-DEWATS-2023-06-C18-002 | A | A-1(H-64) | DEWATS | 18 | 21.1946 | 92.1461 | Effluent | 8.57 | 28.9 | 864 | 12.3 | 54.6 | 204 | 786 | 0 | 5700 | 62.5 | 1.93% | 1040 | 2910
78 | DSK | DPHE-FSL-S-1346 | 16/03/2025 | 18 | IOM | FSTP-18-08 | IOM-DEWATS-2023-06-C18-004 | C | G-43 | DEWATS | 18 | 21.1922 | 92.1476 | Effluent | 7.59 | 29.6 | 956 | 26.7 | 30 | 213 | 873 | 0 | 2700 | 166.66 | 1.69% | 1120 | 3990
79 | DSK | DPHE-FSL-S-1347 | 16/03/2025 | 18 | IOM | FSTP-18-09 | IOM-DEWATS-2023-06-C18-005 | A | A-2(H-62) | DEWATS | 18 | 21.1924 | 92.1479 | Effluent | 8.24 | 28.8 | 924 | 22.4 | 5.6 | 189 | 957 | 0 | 10500 | 133.33 | 3% | 480 | 3350
80 | DSK | DPHE-FSL-S-1348 | 16/03/2025 | 18 | IOM | FSTP-18-11 | IOM-DEWATS-2023-06-C18-003 | B | H-61 | DEWATS | 18 | 21.1904 | 92.1459 | Effluent | 8.04 | 26 | 826 | 70.7 | 1.26 | 171 | 774 | 0 | 3300 | 80 | 1.63% | 1560 | 2220
81 | WVI | DPHE-FSL-S-1349 | 17/03/2025 | 13 | IOM | FSTP-13-10 | WSP-02 | A | A-6 | WSP | 25 | 21.1769 | 92.1419 | Effluent | 7.7 | 26.5 | 512 | 14.4 | 7.12 | 196 | 494 | 300 | 33600 | 100 | 2.94% | 200 | 1980
82 | SHED | DPHE-FSL-S-1350 | 17/03/2025 | 13 | IOM | FSTP-13-09 | IOM-DEWATS-22-06-C-13-0013 | C | C-1 | DEWATS | 18 | 21.1771 | 92.141 | Effluent | 7.82 | 28.7 | 586 | 53.5 | 5.84 | 200 | 258 | 14100 | 19700 | 10 | 1.98% | 240 | 2010
83 | SHED | DPHE-FSL-S-1351 | 17/03/2025 | 13 | IOM | FSTP-13-07 | IOM-DEWATS-2020-09-001 | E | E-1 | DEWATS | 18 | 21.1775 | 92.1365 | Effluent | 7.73 | 28.3 | 836 | 16.5 | 37.4 | 233 | 631 | 0 | 0 | 200 | 2.72% | 160 | 3140
84 | SHED | DPHE-FSL-S-1352 | 17/03/2025 | 13 | IOM | FSTP-13-08 | IOM-DEWATS-2020-09-002 | E | E-1 | DEWATS | 18 | 21.1776 | 92.1365 | Effluent | 7.69 | 28.4 | 830 | 22.7 | 40.4 | 205 | 531 | 0 | 8700 | 80 | 2.97% | 240 | 2640
85 | SHED | DPHE-FSL-S-1353 | 17/03/2025 | 13 | IOM | FSTP-13-01 | WVI-003 | E | E-1 | WSP | 25 | 21.1776 | 92.1366 | Effluent | 8.42 | 29.5 | 610 | 11 | 52 | 244 | 459 | 500 | 6100 | 40 | 1.99% | 640 | 1780
86 | BDRCS | DPHE-FSL-S-1354 | 17/03/2025 | 13 | IOM | FSTP-13-02 | PA-FSTP-01 | G | G-1 | UFF | 25 | 21.1719 | 92.1344 | Effluent | 8.19 | 27.7 | 842 | 15.4 | 75 | 177 | 612 | 3100 | 14500 | 140 | 4.27% | 80 | 2480
87 | BDRCS | DPHE-FSL-S-1355 | 17/03/2025 | 13 | IOM | FSTP-13-03 | PA-FSTP-02 | G | G-3 | UFF | 25 | 21.1817 | 92.1364 | Effluent | 8.42 | 31.2 | 712 | 15.2 | 70.2 | 216 | 905 | 0 | 0 | 140 | 3.99% | 440 | 3230
88 | NRC | DPHE-FSL-S-1356 | 17/03/2025 | 13 | IOM | FSTP-13-05 | NRC- UFF-04 | F | F-4 | UFF | 25 | 21.1808 | 92.1375 | Effluent | 8.56 | 29.3 | 1112 | 16.7 | 29.8 | 203 | 1116 | 0 | 0 | 300 | 3.79% | 960 | 3650
89 | NRC | DPHE-FSL-S-1357 | 17/03/2025 | 13 | IOM | FSTP-13-06 | IOM-DEWATS-2022-08-C13-004 | F | F-2 | DEWATS | 6 | 21.1819 | 92.1404 | Effluent | 8.25 | 28.3 | 820 | 16.9 | 32 | 196 | 673 | 0 | 0 | 250 | 3.21% | 840 | 3770
90 | DSK | DPHE-FSL-S-1358 | 18/03/2025 | 16 | UNICEF | FSTP-16-07 | DSKIVY-16-ABR-004-2020 | C | C-5 | ABR | 35 | 21.1536 | 92.152 | Effluent | 8.75 | 25 | 468 | 141 | 15.28 | 209 | 904 | 0 | 29600 | 250 | 3.73% | 1560 | 2830
91 | DSK | DPHE-FSL-S-1359 | 18/03/2025 | 16 | UNICEF | FSTP-16-05 | DSK-BRAC-EKN-16-ABR-03/19 | C | C-1 | ABR | 35 | 21.1539 | 92.1518 | Effluent | 8.75 | 27.2 | 1408 | 15.7 | 19.88 | 218 | 770 | 0 | 30600 | 150 | 4.27% | 320 | 3340
92 | DSK | DPHE-FSL-S-1360 | 18/03/2025 | 16 | UNICEF | FSTP-16-02 | DSK-Unicef-16-UFF-002/2020 | A | A-5 | UFF | 10 | 21.1596 | 92.1516 | Effluent | 8.53 | 28 | 708 | 17.1 | 90.6 | 231 | 1359 | 300 | 27900 | 450 | 3.65% | 1320 | 3230
93 | DSK | DPHE-FSL-S-1361 | 18/03/2025 | 16 | UNICEF | FSTP-16-04 | C-16-D-08-ABR-007 | D | D-8 | ABR | 30 | 21.1542 | 92.145 | Effluent | 8.35 | 29.5 | 1324 | 13.5 | 34.8 | 179 | 554 | 700 | 4700 | 60 | 2.01% | 120 | 3210
94 | DSK | DPHE-FSL-S-1362 | 18/03/2025 | 16 | UNICEF | FSTP-16-06 | C-16-D-02-UFF-006 | D | D-2 | UFF | 10 | 21.1522 | 92.1501 | Effluent | 8.11 | 29.6 | 912 | 18.4 | 89.6 | 356 | 1613 | 1900 | 4500 | 600 | 4.51% | 1960 | 2280
95 | DSK | DPHE-FSL-S-1363 | 18/03/2025 | 16 | UNICEF | FSTP-16-01 | C-16-B-02-ABR-002 | B | B-4 | ABR | 35 | 21.1565 | 92.1493 | Effluent | 8.15 | 30 | 936 | 20.9 | 81.2 | 406 | 1820 | 0 | 12600 | 666.66 | 3.74% | 1280 | 2950
96 | DSK | DPHE-FSL-S-1364 | 18/03/2025 | 16 | UNICEF | FSTP-16-03 | DSK-Unicef-16-ABR-001/2019 | A | A-2 | ABR | 30 | 21.1582 | 92.1488 | Effluent | 8.75 | 29.5 | 750 | 20.7 | 114.2 | 476 | 1796 | 0 | 400 | 700 | 3.36% | 2000 | 3130
97 | BRAC | DPHE-FSL-S-1365 | 18/03/2025 | 21 | UNHCR | FSTP-21-02 | C-21-ABR-Omani | C | Omani Play Ground | ABR | 60 | 21.1318 | 92.1608 | Effluent | 8.45 | 34.5 | 714 | 18.3 | 60.8 | 391 | 1392 | 400 | 1000 | 500 | 3.45% | 1000 | 3080
98 | NGOF | DPHE-FSL-S-1366 | 2025-07-04 | 9 | IOM | FSTP-09-01 | IOM-DEWATS-2021-11-C-9-004 | F | G-3 | DEWATS | 18 | 21.1893 | 92.1589 | Effluent | 8.17 | 30.8 | 985 | 19.5 | 44 | 136 | 739 | 0 | 0 | 250 | 5.2% | 320 | 4450
99 | NGOF | DPHE-FSL-S-1367 | 2025-07-04 | 9 | IOM | FSTP-09-04 | IOM-DEWATS-2021-07-C09-003 | F | C-17 | DEWATS | 18 | 21.188 | 92.1604 | Effluent | 7.77 | 26.2 | 644 | 23.5 | 43.9 | 90 | 340 | 3600 | 36000 | 100 | 4.1% | 40 | 2930
100 | DSK | DPHE-FSL-S-1368 | 2025-07-04 | 22 | UNICEF | FSTP-22-01 | DSK-UNICEF-22-ABR-01/2020 | A | A-1 | ABR | 50 | 21.0878 | 92.2006 | Effluent | 8.07 | 30.1 | 1010 | 14.4 | 38 | 190 | 1104 | 100 | 400 | 300 | 4.78% | 40 | 3200
101 | DSK | DPHE-FSL-S-1369 | 2025-07-04 | 22 | UNICEF | FSTP-22-03 | DSK-UNICEF-22-ABR-03/2021 | C | C-3 | ABR | 60 | 21.0876 | 92.1936 | Effluent | 8.2 | 30.3 | 1020 | 14.2 | 48.2 | 180 | 1021 | 100 | 100 | 300 | 4.78% | 880 | 2900
102 | DSK | DPHE-FSL-S-1370 | 2025-07-04 | 22 | UNICEF | FSTP-22-02 | DSK-UNICEF-22-ABR-02/2020 | C | C-3 | ABR | 60 | 21.0876 | 92.1938 | Effluent | 8.69 | 31.2 | 901 | 15 | 48.5 | 137 | 877 | 0 | 2900 | 250 | 5.39% | 40 | 2300
103 | DSK | DPHE-FSL-S-1371 | 2025-09-04 | 24 | IOM | FSTP-24-01 | FSM-Capm-24-01 | E | E-5 | DEWATS | 18 | 21.975 | 92.2423 | Effluent | 9.15 | 30.8 | 351 | 11.3 | 21.9 | 44 | 378 | 7900 | 19600 | 125 | 4.55% | 40 | 2270
104 | DSK | DPHE-FSL-S-1372 | 2025-09-04 | 24 | IOM | FSTP-24-03 | DEWATS-03 | E | E-5 | DEWATS | 15 | 21.9712 | 92.2435 | Effluent | 9.06 | 30.1 | 449 | 9.71 | 22.5 | 71 | 473 | 0 | 1900 | 150 | 4.55% | 40 | 2610
105 | DSK | DPHE-FSL-S-1373 | 2025-09-04 | 24 | IOM | FSTP-24-02 | DEWATS-Unit-04 | D | D-2 | DEWATS | 40 | 20.9751 | 92.2424 | Effluent | 8.05 | 29.4 | 113 | 2.11 | 8.57 | 45 | 170 | 23600 | 53900 | 40 | 0.9% | 80 | 300
106 | DSK | DPHE-FSL-S-1374 | 2025-09-04 | 24 | IOM | FSTP-24-06 | IOM-DEWATS-2023-01-C-24-002 | D | D-3 | DEWATS | 6 | 20.9695 | 92.2433 | Effluent | 8.85 | 30.8 | 742 | 15.4 | 38.7 | 139 | 1232 | 200 | 3800 | 300 | 4.59% | 1240 | 3860
107 | ANANDA | DPHE-FSL-S-1375 | 2025-09-04 | 24 | IOM | FSTP-24-04 | IOM-DEWATS-01 | B | B-4 | DEWATS | 18 | 20.9551 | 92.2424 | Effluent | 8.38 | 31.2 | 311 | 26.8 | 65.1 | 145 | 659 | 0 | 0 | 25 | 4.78% | 80 | 1610
108 | ANANDA | DPHE-FSL-S-1376 | 2025-09-04 | 24 | IOM | FSTP-24-05 | IOM-DEWATS-02 | B | B-4 | DEWATS | 18 | 20.9551 | 92.2424 | Effluent | 9.2 | 32.8 | 989 | 23.9 | 37.4 | 170 | 970 | 0 | 0 | 50 | 3.84% | 600 | 3740
109 | SCI | DPHE-FSL-S-1377 | 2025-09-04 | 25 | IOM | FSTP-25-01 | SCI-C25-Alikhali-DEWATS-FSTP-02 | D | D-9 | DEWATS | 30 | 20.9785 | 92.2426 | Effluent | 8.7 | 31.2 | 856 | 14.6 | 44.4 | 118 | 681 | 1100 | 3500 | 133.33 | 3.47% | 40 | 2250
110 | BRAC | DPHE-FSL-S-1378 | 2025-09-04 | 25 | IOM | FSTP-25-02 | C-25-B-1-FSTP-001 | B | B-1 | ABR | 30 | 21.144 | 92.1946 | Effluent | 9.19 | 30.3 | 1240 | 25.1 | 43.1 | 212 | 1688 | 500 | 4600 | 450 | 5.72% | 40 | 4220
111 | SHED | DPHE-FSL-S-1379 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -13 | IOM-DLT-001(KSR-19) | S-1 | B-4 | SSU | 16 | 21.1868 | 92.1359 | Effluent | 8.78 | 28.6 | 202 | 14.1 | 11.8 | 412 | 446 | 10500 | 18700 | 40 | 1.04% | 240 | 1460
112 | SHED | DPHE-FSL-S-1380 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -15 | IOM-DLT-002(KSR-29) | S-3 | B-5 | SSU | 16 | 21.1909 | 92.1342 | Effluent | 8.94 | 31.2 | 484 | 21.4 | 59.9 | 330 | 924 | 3800 | 17500 | 125 | 0.83% | 40 | 2130
113 | SHED | DPHE-FSL-S-1381 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -19 | IOM-DLT-005(KSR-23) | S-3 | B-4 | SSU | 16 | 21.1984 | 92.1359 | Effluent | 8.98 | 31.1 | 413 | 117.1 | 15 | 315 | 1350 | 1900 | 36000 | 133.33 | 0.91% | 160 | 2290
114 | SHED | DPHE-FSL-S-1382 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -16 | IOM-DEWATS-2023-06-C-20Ext-002 | S-2 | B-1 | DEWATS | 20 | 21.1918 | 92.134 | Effluent | 7.21 | 31.9 | 291 | 22.9 | 13.9 | 491 | 360 | 200 | 17500 | 70 | 1.01% | 80 | 1810
115 | SHED | DPHE-FSL-S-1383 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -09 | IOM-DLT-003(KSR-21) | S-3 | B-4 | DEWATS | 16 | 21.1916 | 92.1331 | Effluent | 7.7 | 29.8 | 1010 | 14.8 | 53.5 | 156 | 913 | 0 | 0 | 200 | 2.25% | 200 | 4180
116 | SHED | DPHE-FSL-S-1384 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -12 | IOM-DLT-008(KSR-26) | S-3 | B-1 | SSU | 16 | 21.1945 | 92.1339 | Effluent | 8.66 | 29.8 | 571 | 14.6 | 29.6 | 41 | 1293 | 0 | 81100 | 150 | 0.82% | 120 | 2600
117 | SHED | DPHE-FSL-S-1385 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -08 | IOM-DLT-005(KSR-24) | S-3 | B-3 | DEWATS | 16 | 21.1943 | 92.1321 | Effluent | 9.09 | 30.2 | 581 | 30.3 | 3.99 | 316 | 550 | 0 | 0 | 57.14 | 1.42% | 760 | 1270
118 | SHED | DPHE-FSL-S-1386 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -20 | IOM-DLT-009(KSR-27) | S-2 | B-5 | DEWATS | 16 | 21.1945 | 92.1335 | Effluent | 6.83 | 29.4 | 63.9 | 39 | 2.44 | 286 | 129 | 2500 | 7500 | 10 | 0.41% | 200 | 940
119 | SHED | DPHE-FSL-S-1387 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -11 | IOM-DLT-10(KSR-28) | S-4 | B-7 | SSU | 16 | 21.1984 | 92.1359 | Effluent | 9.04 | 30.8 | 580 | 15.9 | 36.5 | 236 | 1067 | 3100 | 29600 | 166.66 | 2.44% | 280 | 2960
120 | SHED | DPHE-FSL-S-1388 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -14 | IOM-DLT-004(KSR-15) | S-2 | B-2 | DEWATS | 16 | 21.1944 | 92.1365 | Effluent | 9.02 | 31.7 | 180 | 35.3 | 26.8 | 319 | 574 | 0 | 5100 | 40 | 0.81% | 120 | 1800
121 | SHED | DPHE-FSL-S-1389 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -23 | IOM-DLT-015(KSR-30) | S | B-2 | SSU | 15 | 21.1935 | 92.137 | Effluent | 8.95 | 29.3 | 421 | 7.05 | 60.5 | 506 | 519 | 11900 | 59700 | 166.66 | 1% | 120 | 2830
122 | SHED | DPHE-FSL-S-1390 | 15/04/2025 | 20 | IOM | FSTP-20 -16 | IOM-DLT-004(KSR-14) | A | M-35 | DEWATS | 18 | 21.192 | 92.1414 | Effluent | 8.17 | 29.5 | 781 | 11.2 | 5.25 | 175 | 465 | 0 | 0 | 100 | 1.21% | 80 | 2300
123 | SHED | DPHE-FSL-S-1391 | 15/04/2025 | 20 | IOM | FSTP-20 -04 | IOM-DLT-008(KSR-18) | B | M-31 | SSU | 20 | 21.1912 | 92.1385 | Effluent | 7.95 | 29.6 | 703 | 17.2 | 50.4 | 128 | 1266 | 0 | 0 | 433.33 | 2.44% | 120 | 2240
124 | SHED | DPHE-FSL-S-1392 | 15/04/2025 | 20 | IOM | FSTP-20 -05 | IOM-DLT-003(KSR-13) | A | M-30 | DEWATS | 18 | 21.1929 | 92.1435 | Effluent | 8.95 | 29.8 | 410 | 18.2 | 47.9 | 492 | 694 | 0 | 0 | 100 | 2.03% | 200 | 3050
125 | SHED | DPHE-FSL-S-1393 | 15/04/2025 | 20 | IOM | FSTP-20 -03 | IOM-DLT-006(KSR-16) | A | M-27 | SSU | 14 | 21.1909 | 92.1403 | Effluent | 8.15 | 28.8 | 755 | 8.35 | 37.1 | 39 | 381 | 0 | 0 | 20 | 1.2% | 360 | 2950
126 | SHED | DPHE-FSL-S-1394 | 15/04/2025 | 20 | IOM | FSTP-20 -02 | IOM-DLT-2018-10-C-20(KSR-11) | A | M-22 | SSU | 14 | 21.1935 | 92.1429 | Effluent | 8.29 | 29.3 | 657 | 20.2 | 51.1 | 117 | 1972 | 0 | 900 | 300 | 2.7% | 240 | 2120
127 | SCI | DPHE-FSL-S-1395 | 15/04/2025 | 20 | IOM | FSTP-20 -07 | SCI-FSTP-01 | B | M-24 | ABR | 20 | 21.1877 | 92.1407 | Effluent | 8.53 | 29.5 | 65.8 | 26.5 | 6.65 | 602 | 92.2 | 0 | 1100 | 30 | 1.83% | 160 | 2170
128 | SHED | DPHE-FSL-S-1396 | 15/04/2025 | 20 | IOM | FSTP-20-01 | IOM-DLT-007-KSR-17 | B | M-39 | SSU | 14 | 21.1888 | 92.1395 | Effluent | 8.19 | 30.3 | 153 | 8.47 | 47.2 | 326 | 248 | 2900 | 8700 | 20 | 0.81% | 200 | 2160
129 | CARE BANGLADESH | DPHE-FSL-S-1397 | 16/04/25 | 15 | UNICEF | FSTP-15-01 | UFF-01 | A | A-5 | UFF | 15 | 21.1621 | 92.1502 | Effluent | 8.08 | 27.6 | 936 | 27.5 | 62.3 | 489 | 1496 | 1100 | 12600 | 600 | 2.44% | 120 | 3380
130 | CARE BANGLADESH | DPHE-FSL-S-1398 | 16/04/25 | 15 | UNICEF | FSTP-15-02 | WSP-02 | A | A-8 | WSP | 35 | 21.1639 | 92.1496 | Effluent | 8.73 | 30.8 | 525 | 14.8 | 8.89 | 212 | 775 | 6500 | 19600 | 250 | 1.22% | 200 | 2950
131 | CARE BANGLADESH | DPHE-FSL-S-1399 | 16/04/25 | 15 | UNICEF | FSTP-15-03 | ABR-03 | B | B-2 | ABR | 35 | 21.1613 | 92.147 | Effluent | 8.79 | 31.7 | 836 | 20.2 | 71.7 | 281 | 1378 | 1700 | 16800 | 500 | 2.01% | 600 | 3250
132 | CARE BANGLADESH | DPHE-FSL-S-1400 | 16/04/25 | 15 | UNICEF | FSTP-15-19 | UFF-04 | C | C-4 | UFF | 15 | 21.1613 | 92.1445 | Effluent | 8.72 | 30.9 | 650 | 27 | 52.3 | 79 | 849 | 9500 | 3600 | 33.33 | 2.24% | 40 | 3100
133 | CARE BANGLADESH | DPHE-FSL-S-1401 | 16/04/25 | 15 | UNICEF | FSTP-15-04 | WSP-05 | C | C-10 | WSP | 35 | 21.1638 | 92.1443 | Effluent | 7.95 | 31 | 185 | 18.9 | 6.5 | 182 | 384 | 500 | 48500 | 50 | 1.21% | 320 | 3570
134 | CARE BANGLADESH | DPHE-FSL-S-1402 | 16/04/25 | 15 | UNICEF | FSTP-15-05 | UFF-06 | D | D-11 | UFF | 15 | 21.163 | 92.1435 | Effluent | 8.8 | 31.7 | 1060 | 32.1 | 83.7 | 394 | 1407 | 0 | 0 | 400 | 2.82% | 160 | 3500
135 | MSF-Hospital | DPHE-FSL-S-1403 | 16/04/25 | 15 | UNICEF | FSTP-15-23 |  | C | C-6 | DEWATS | 105 | 21.1611 | 92.1429 | Effluent | 7.85 | 29.7 | 82 | 1.86 | 20.2 | 133 | 209 | 116500 | 116500 | 80 | 0.43% | 80 | 1950
136 | CARE BANGLADESH | DPHE-FSL-S-1404 | 16/04/25 | 15 | UNICEF | FSTP-15-06 | UFF-07 | D | D-6 | UFF | 15 | 21.162 | 92.142 | Effluent | 8.2 | 31.9 | 521 | 10.2 | 46.3 | 357 | 843 | 89600 | 145600 | 333.33 | 1.63% | 40 | 3190
137 | CARE BANGLADESH | DPHE-FSL-S-1405 | 16/04/25 | 15 | UNICEF | FSTP-15-07 | UFF-10 | E | E-13 | UFF | 15 | 21.162 | 92.1401 | Effluent | 7.8 | 30.2 | 518 | 13.2 | 41.7 | 208 | 1040 | 12000 | 17000 | 100 | 2.05% | 160 | 2560
138 | CARE BANGLADESH | DPHE-FSL-S-1406 | 16/04/25 | 15 | UNICEF | FSTP-15-08 | UFF-08 | D | D-14 | UFF | 15 | 21.1619 | 92.1382 | Effluent | 8.2 | 30.3 | 565 | 10.6 | 72.5 | 133 | 1057 | 16000 | 50100 | 200 | 1% | 80 | 2950
139 | CARE BANGLADESH | DPHE-FSL-S-1407 | 16/04/25 | 15 | UNICEF | FSTP-15-17 | ABR-17 | G | G-8 | ABR | 35 | 21.1578 | 92.1466 | Effluent | 8.21 | 30.8 | 1010 | 19.8 | 56.4 | 1305 | 1611 | 900 | 14500 | 500 | 2.21% | 80 | 3090
140 | CARE BANGLADESH | DPHE-FSL-S-1408 | 16/04/25 | 15 | UNICEF | FSTP-15-22 | UFF-18 | G | G-10 | UFF | 15 | 21.1585 | 92.1472 | Effluent | 8.27 | 30.9 | 222 | 15.3 | 74.7 | 156 | 1087 | 7500 | 19500 | 50 | 1.2% | 80 | 3080
141 | CARE BANGLADESH | DPHE-FSL-S-1409 | 16/04/25 | 15 | UNICEF | FSTP-15-10 | UFF-13 | E | E-3 | UFF | 15 | 21.1585 | 92.1443 | Effluent | 8.36 | 30.6 | 956 | 21.4 | 45 | 352 | 1623 | 3500 | 12500 | 100 | 2.41% | 160 | 3070
142 | CARE BANGLADESH | DPHE-FSL-S-1410 | 16/04/25 | 15 | UNICEF | FSTP-15-20 | UFF-12 | E | E-8 | UFF | 15 | 21.1606 | 92.143 | Effluent | 8.9 | 30.9 | 419 | 7.3 | 28.7 | 135 | 456 | 4500 | 19600 | 60 | 1.44% | 200 | 3310
143 | CARE BANGLADESH | DPHE-FSL-S-1411 | 16/04/25 | 15 | UNICEF | FSTP-15-13 | ABR-14 | F | F-10 | ABR | 35 | 21.1509 | 92.1426 | Effluent | 8.3 | 30.3 | 992 | 21.7 | 63 | 160 | 1140 | 4900 | 19500 | 150 | 0.4% | 120 | 3090
144 | CARE BANGLADESH | DPHE-FSL-S-1412 | 16/04/25 | 15 | UNICEF | FSTP-15-12 | UFF-15 | F | F-7 | UFF | 15 | 21.1584 | 92.1419 | Effluent | 8.33 | 30.8 | 528 | 15.1 | 25.5 | 190 | 492 | 500 | 6500 | 80 | 1.45% | 200 | 2960
145 | CARE BANGLADESH | DPHE-FSL-S-1413 | 16/04/25 | 15 | UNICEF | FSTP-15-14 | UFF-16 | F | F-6 | UFF | 15 | 21.1568 | 92.1436 | Effluent | 8.2 | 30.7 | 372 | 16 | 26.9 | 440 | 1270 | 4100 | 14500 | 150 | 1.21% | 80 | 3080
146 | CARE BANGLADESH | DPHE-FSL-S-1414 | 16/04/25 | 15 | UNICEF | FSTP-15-21 | UFF-19 | H | H-4 | UFF | 15 | 21.1575 | 92.1402 | Effluent | 8.1 | 30.2 | 784 | 47.3 | 70.4 | 365 | 1610 | 6900 | 11100 | 66.66 | 1.22% | 320 | 3010
147 | CARE BANGLADESH | DPHE-FSL-S-1415 | 16/04/25 | 15 | UNICEF | FSTP-15-16 | WSP-22 | H | H-15 | WSP | 35 | 21.1627 | 92.1968 | Effluent | 8.37 | 29.9 | 611 | 23.6 | 43.9 | 156 | 1029 | 112000 | 126000 | 150 | 1.69% | 80 | 2970
148 | CARE BANGLADESH | DPHE-FSL-S-1416 | 16/04/25 | 15 | UNICEF | FSTP-15-11 | UFF-21 | H | H-9 | UFF | 15 | 21.1587 | 92.1372 | Effluent | 8.36 | 30.8 | 405 | 8.16 | 52.3 | 55 | 281 | 3600 | 14000 | 10 | 1% | 200 | 3010
149 | CARE BANGLADESH | DPHE-FSL-S-1417 | 16/04/25 | 15 | UNICEF | FSTP-15-09 | WSP-09 | E | E-16 | WSP | 35 | 21.1629 | 92.1368 | Effluent | 8.95 | 30.7 | 432 | 19.5 | 40.5 | 119 | 521 | 9600 | 20800 | 66.66 | 1% | 320 | 3250
150 | BRAC | DPHE-FSL-S-1418 | 20/04/25 | 14 | UNICEF | FSTP-14-06 | C-14-D-D2-FSM-07 | D | D-2 | ABR | 50 | 21.168 | 92.1424 | Effluent | 8.74 | 29.2 | 324 | 28 | 8.92 | 45 | 207 | 900 | 29600 | 100 | 1.44% | 200 | 1760
151 | BRAC | DPHE-FSL-S-1419 | 20/04/25 | 14 | UNICEF | FSTP-14-03 | C-14-D-D3-FSM-03 | D | D-3 | ABR | 50 | 21.1658 | 92.1439 | Effluent | 8.55 | 30 | 616 | 11.4 | 82 | 170 | 550 | 20500 | 58600 | 550 | 2.65% | 200 | 2480
152 | BRAC | DPHE-FSL-S-1420 | 20/04/25 | 14 | UNICEF | FSTP-14-01 | C-14-A-A4-FSM-04 | A | A-4 | ABR | 50 | 21.1517 | 92.5315 | Effluent | 8.29 | 30.9 | 926 | 20 | 55.8 | 145 | 866 | 4000 | 9600 | 550 | 1.21% | 160 | 2310
153 | BRAC | DPHE-FSL-S-1421 | 20/04/25 | 14 | UNICEF | FSTP-14-05 | C-14-E-E1-FSM-01 | E | E-1 | ABR | 50 | 21.1664 | 92.1407 | Effluent | 8.53 | 27.7 | 240 | 5.97 | 9.22 | 80 | 155 | 800 | 19000 | 20 | 0.65% | 160 | 510
154 | BRAC | DPHE-FSL-S-1422 | 20/04/25 | 14 | UNICEF | FSTP-14-07 | C-14-C-C2-FSM-05 | C | C-2 | ABR | 55 | 21.1705 | 92.1472 | Effluent | 6.89 | 28 | 145 | 45.9 | 10.82 | 42 | 170 | 10800 | 20600 | 40 | 0.82% | 120 | 1090

## Comparision with Previous round
Analysis Data comparison with previous round and 2025
Year | Round | Summary of FSTP Effluent analysis by DPHE FSL | Parameters
|  |  | pH | Temp (0C) | BOD (mg/L) | COD (mg/L) | Total Nitrogen (mg/L) | Nitrate (mg/L) | Phosphate (mg/L) | TSS (mg/l) | Total Coliforms (cfu/100 ml) | Oil & Grease (mg/L)
Govt Std (DoE 2019) |  |  | 6 to 9 | 30 | 30 | 200 | 15 | 250 | 35 | 100 | 1000
2022 | 1st | % of FSTPs above limit | 6% | 7% | 97% | 92% | 99% | 2% | 18% | 57% | 98%
| 2nd | % of FSTPs above limit | 3% | 51% | 94% | 88% | 100% | 2% | 53% | 41% | 94%
| 3rd | % of FSTPs above limit | 2% | 9% | 84% | 70% | 95% | 0.49% | 42% | 28% | 86%
Govt Std (DoE 2023) |  |  | 6 to 9 | 30 | 30 | 125 | N/A | 50 | 15 | 100 | 1000 | 10
2023 | 1st | % of FSTPs above limit | 7.9% | 5.2% | 90.6% | 88.5% | N/A | 10.99% | 87.96% | 45% | 94.8% | N/A
| 2nd | % of FSTPs above limit | 0% | 70.1% | 95.8% | 93.4% | N/A | 12.6% | 43.1% | 38.92% | 93.4% | N/A
| 3rd | % of FSTPs above limit | 1.2% | 36.9% | 93.5% | 89.9% | N/A | 9.5% | 68.5% | 45.2% | 90.5% | 99.4%
Govt Std (DoE 2023) |  |  | 6 to 9 | 30 | 30 | 125 | N/A | 50 | 15 | 100 | 1000 | 10
2024 | 1st | % of FSTPs above limit | 6.494% | 29.22% | 100% | 98.7% | N/A | 13.64% | 74.03% | 53.9% | 75.32% | 100%
| 2nd | % of FSTPs above limit
| 3rd | % of FSTPs above limit
Govt Std (DoE 2023) |  |  | 6 to 9 | 30 | 30 | 125 | N/A | 50 | 15 | 100 | 1000 | 10
2025 | 1st | % of FSTPs above limit | 4% | 21% | 100% | 99% | N/A | 12% | 73% | 62% | 75% | 100%
| 2nd | % of FSTPs above limit
| 3rd | % of FSTPs above limit

## Technologywise data comparision
Treatment Technology wise effluent's analysis data comparision (average)-2025
S/N | Technology Type | Functional FSTP Qty | pH | TN (mg/l) | Nitrate (mg/l) | Phosphate (mg/l) | BOD (mg/l) | COD (mg/l) | E.Coli (cfu/100 ml) | Total Coliform (Cfu/100 ml) | TSS (mg/l) | TS (%) | Oil & Grease (mg/l)
1 | ABR | 44 | 8.42 | 628.61 | 38.29 | 46.53 | 254 | 874 | 5145 | 16982 | 232 | 2.64 | 462
2 | ADS | 1 | 8.27 | 401 | 350 | 18.98 | 130 | 380 | 1000 | 4700 | 57 | 2.58 | 432
3 | Anaerobic Lagoon | 2 | 8.52 | 382 | 150.5 | 13.23 | 91 | 414 | 2100 | 34300 | 30 | 2.81 | 522
4 | Biological Process | 4 | 8.46 | 290 | 164.65 | 31.5 | 159 | 540 | 500 | 27050 | 125 | 2.02 | 340
5 | DEWATS | 43 | 8.13 | 585 | 27.09 | 35.53 | 199 | 613 | 4135 | 11797 | 141 | 2.31 | 466
7 | LSP | 2 | 9.11 | 884 | 23.45 | 10.64 | 301 | 1095 | 800 | 3100 | 175 | 1.87 | 1281
8 | Omni processor | 1 | 7.48 | 378 | 23.2 | 26.6 | 115 | 308 | 2400 | 44400 | 166.66 | 0.61 | 920
9 | SSU | 13 | 8.6 | 548 | 24.9 | 44.13 | 267 | 1027 | 2623 | 22869 | 171 | 1.67 | 273
10 | UFF | 32 | 8.32 | 582 | 26.11 | 51.98 | 254 | 990 | 15309 | 24340 | 210 | 7.29 | 430
11 | WSP | 12 | 8.29 | 391 | 25.64 | 19.18 | 160 | 526 | 11291 | 25400 | 100 | 6.13 | 260
Total Functional FSTPs |  | 154

## Sheet2
Row Labels | Average of Total Coliform (Cfu/100 ml)
ABR | 16981.8182
ADS | 47000
Anarobic Legone | 27500
Biological Process | 28633.3333
DEWATS | 11797.6744
LSP | 3100
Omni Processor | 44400
SSU | 22869.2308
UFF | 24340.625
WSP | 25400
Grand Total | 18726.9737

## Sheet1
S/N | Organization | Sample ID | Sample Collection | Camp ID | WASH AFA | FSTP ID (By DPHE) | FSTP ID (Organization) | Block | Sub Block | Technology Type | Capacity (m3/week) | Latitude | Longitude | Sample Type | pH | Temperature (Degree C) | TN (mg/l) | Nitrate (mg/l) | Phosphate (mg/l) | BOD (mg/l) | COD (mg/l) | E.Coli (cfu/100 ml) | Total Coliform (Cfu/100 ml) | TSS (mg/l) | TS (%) | Oil & Grease (mg/l) | Conductivity (µS/cm) | Incharge of FSTP | Contact Number | Alternative Number |  | Remarks
1 | NGOF | DPHE-FSL-S-1269 | 18/02/2025 | 7 | UNICEF | FSTP-07-03 | UFF-02 | B | B5 | UFF | 15 | 21.2039 | 92.1677 | Effluent | 8.34 | 25.4 | 466 | 30 | 82.8 | 260 | 906 | 0 | 0 | 171.42 | 38.84% | 612 | 6500
2 | NGOF | DPHE-FSL-S-1270 | 18/02/2025 | 7 | UNICEF | FSTP-07-01 | UFF-05 | A | A7 | UFF | 30 | 21.2056 | 92.1697 | Effluent | 8.28 | 26.3 | 601 | 44.8 | 50.8 | 380 | 1103 | 0 | 0 | 266.66 | 27.12% | 496 | 8970
3 | NGOF | DPHE-FSL-S-1271 | 18/02/2025 | 7 | UNICEF | FSTP-07-02 | UFF-01 | B | B1 | UFF | 15 | 21.2056 | 92.1697 | Effluent | 7.94 | 29.4 | 1040 | 39.3 | 101.2 | 620 | 1777 | 0 | 0 | 333.33 | 41.27% | 928 | 8250 |  |  |  | 33
4 | NGOF | DPHE-FSL-S-1272 | 18/02/2025 | 7 | UNICEF | FSTP-07-07 | UFF-09 | C | C-1 | UFF | 15 | 21.2045 | 92.1663 | Effluent | 8.69 | 26.3 | 640 | 105 | 51.6 | 280 | 890 | 100 | 12800 | 37.04 | 64.27% | 1776 | 6040
5 | NGOF | DPHE-FSL-S-1273 | 18/02/2025 | 7 | UNICEF | FSTP-07-08 | WVI WSP-03 | C | C1 | WSP | 15 | 21.2036 | 92.1656 | Effluent | 8.75 | 26.9 | 691 | 58.9 | 31.2 | 312 | 912 | 1100 | 7100 | 266.66 | 51.75% | 218 | 4270
6 | NGOF | DPHE-FSL-S-1274 | 23/02/2025 | 26 | UNHCR | FSTP-26-03 | NGOF-C26-ADS-01 | I | I-5 | ADS | 25 | 20.9661 | 92.2453 | Effluent | 8.27 | 31.8 | 401 | 350 | 18.98 | 130 | 380 | 1000 | 47000 | 57.14 | 2.58% | 432 | 4220
7 | NGOF | DPHE-FSL-S-1275 | 23/02/2025 | 26 | UNHCR | FSTP-26-04 | FSTP-03 (Mega FSTP-03) | G | G1 | Biological Process | 350 | 21.2096 | 92.2528 | Effluent | 7.77 | 30.4 | 590 | 257 | 28.2 | 55 | 490 | 900 | 50900 | 40 | 2.83% | 444 | 6170 |  |  |  | 0.21711
8 | NGOF | DPHE-FSL-S-1276 | 23/02/2025 | NRC | UNHCR | FSTP-NRC-01 | NGOF-NRC- ABR-01 | C |  | ABR | 10 | 20.9529 | 92.2513 | Effluent | 8.86 | 27.1 | 1198 | 25.7 | 50.2 | 155 | 789 | 600 | 8900 | 250 | 2.66% | 296 | 4920
9 | TDH | DPHE-FSL-S-1277 | 23/02/2025 | 27 | UNHCR | FSTP-27-03 | C-27-TDH-LSP | A |  | LSP | 25 | 20.9474 | 92.2606 | Effluent | 8.98 | 27.2 | 1388 | 28.9 | 9.96 | 197 | 971 | 0 | 1500 | 250 | 1.94% | 242 | 5650
10 | NGOF | DPHE-FSL-S-1278 | 23/02/2025 | 27 | UNHCR | FSTP-27-01 | NGOF-C-27-ABR-01 | C | C-10 | ABR | 50 | 20.9031 | 92.262 | Effluent | 8.77 | 31.1 | 396 | 19.4 | 6.8 | 248 | 1434 | 0 | 0 | 200 | 2.21% | 492 | 5890
12 | NGOF | DPHE-FSL-S-1280 | 24/02/2025 | 7 | UNICEF | FSTP-07-06 | WSP-02 | C | C-2 | WSP | 15 | 21.2036 | 92.1655 | Effluent | 8.74 | 26.1 | 164 | 57.8 | 4.96 | 61 | 141 | 0 | 300 | 20 | 0.5% | 144 | 1600
13 | NGOF | DPHE-FSL-S-1281 | 24/02/2025 | 7 | UNICEF | FSTP-07-13 | UFF-07 | E | E2 | UFF | 30 | 21.2019 | 92.1639 | Effluent | 8.46 | 25 | 205 | 24.2 | 3.6 | 39 | 189 | 3400 | 35000 | 10 | 0.34% | 120 | 2090
14 | NGOF | DPHE-FSL-S-1282 | 24/02/2025 | 7 | UNICEF | FSTP-07-12 | ABR-01 | E | E-6 | ABR | 45 | 21.2017 | 92.1625 | Effluent | 8.68 | 24.3 | 353.3 | 29.3 | 62.6 | 265 | 1004 | 200 | 2600 | 66.66 | 1.93% | 104 | 6670
15 | NGOF | DPHE-FSL-S-1283 | 24/02/2025 | 7 | UNICEF | FSTP-07-15 | ABR-04 | G | G-6 | ABR | 15 | 21.2017 | 92.1612 | Effluent | 8.6 | 25.8 | 385 | 41 | 25.6 | 178 | 714 | 100 | 1100 | 100 | 1.63% | 188 | 6200
16 | NGOF | DPHE-FSL-S-1284 | 24/02/2025 | 7 | UNICEF | FSTP-07-14 | ABR-04 | G | G-5 | ABR | 15 | 21.2008 | 92.1597 | Effluent | 8.26 | 25.6 | 417 | 26.3 | 103 | 370 | 1126 | 1000 | 1500 | 300 | 1.71% | 120 | 7710
17 | NGOF | DPHE-FSL-S-1285 | 24/02/2025 | 7 | UNICEF | FSTP-07-11 | UFF-06 | E | E-2 | UFF | 20 | 21.2033 | 92.1618 | Effluent | 8.14 | 26.8 | 308.7 | 30.4 | 112.8 | 480 | 1343 | 0 | 500 | 400 | 2.71% | 152 | 7910
18 | NGOF | DPHE-FSL-S-1286 | 24/02/2025 | 7 | UNICEF | FSTP-07-04 | UFF-04 | D | D-4 | UFF | 15 | 21.2087 | 92.1545 | Effluent | 8.96 | 25.6 | 443.1 | 29.6 | 39.4 | 448 | 1226 | 1000 | 2100 | 266.66 | 1.83% | 600 | 3260
19 | NGOF | DPHE-FSL-S-1287 | 24/02/2025 | 7 | UNICEF | FSTP-07-05 | ABR-03 | D | D-6 | ABR | 15 | 21.2026 | 92.1651 | Effluent | 8.74 | 26.1 | 305.1 | 25.7 | 37.2 | 79 | 410 | 300 | 12700 | 20 | 1.11% | 112 | 2210
21 | BRAC | DPHE-FSL-S-1289 | 2025-02-03 | Kutupalong | UNHCR | FSTP-H-01 | FSTP-02 (Mega FSTP) | E | A-14 | Biological Process | 455 | 21.2102 | 92.1698 | Effluent | 8.45 | 28.4 | 195 | 352 | 40 | 91 | 395 | 100 | 31300 | 140 | 1.84% | 196 | 8460
22 | BRAC | DPHE-FSL-S-1290 | 25/02/25 | 1E | UNHCR | FSTP-H-01-01 | 1-E ABR | B | B-12 | ABR | 15 | 21.2194 | 92.1512 | Effluent | 7.97 | 25.1 | 848 | 25.1 | 95 | 187 | 479 | 0 | 5700 | 200 | 1.22% | 720 | 3190
23 | BRAC | DPHE-FSL-S-1291 | 25/02/2025 | 1W | UNHCR | FSTP-01-02 | 1W ABR | E | E-2 | ABR | 50 | 21.0613 | 92.1538 | Effluent | 8.53 | 25.2 | 1120 | 29.4 | 96.2 | 480 | 1116 | 0 | 0 | 150 | 2.4% | 760 | 4380
24 | WB | DPHE-FSL-S-1292 | 25/02/2025 | 2W | DPHE | FSTP-02-01 | Package(WB-09) | B | B-6 | ABR | 64 | 21.2068 | 92.1598 | Effluent | 8.61 | 28.6 | 314 | 338 | 8.52 | 384 | 493 | 6700 | 36700 | 100 | 2.25% | 840 | 3260
25 | DPHE | DPHE-FSL-S-1293 | 25/02/2025 | 12 | WB | FSTP-12-05 | WD-09, ABR | G-13 | C-3 | ABR | 36 | 21.1815 | 92.148 | Effluent | 9 | 29.5 | 338 | 178 | 26.2 | 365 | 677 | 0 | 6500 | 30 | 1.82% | 144 | 1560
26 | DSK | DPHE-FSL-S-1294 | 25/02/2025 | 12 | IOM | FSTP-12-03 | IOM-DEWATS-2023-01,C-12-003 | C | J-12 | DEWATS | 18.6 | 21.1824 | 92.1481 | Effluent | 7.91 | 27.2 | 188 | 49.7 | 1.5 | 76 | 149 | 0 | 1900 | 100 | 1.81% | 1000 | 1430
27 | DSK | DPHE-FSL-S-1295 | 25/02/2025 | 12 | IOM | FSTP-12-04 | IOM-DEWATS-2023-02,C-12-004 | C | J-12 | DEWATS | 18.6 | 21.1831 | 92.1483 | Effluent | 7.92 | 27.3 | 788 | 27 | 32.4 | 306 | 497 | 0 | 0 | 60 | 1.24% | 840 | 3100
28 | DSK | DPHE-FSL-S-1296 | 25/02/2025 | 12 | IOM | FSTP-12-01 | IOM-DEWATS-2020-09,C-12-001 | A | G-9 | DEWATS | 18.6 | 21.1788 | 92.1539 | Effluent | 8.24 | 27.4 | 125.2 | 65.3 | 19.46 | 45 | 172 | 0 | 100 | 200 | 1.02% | 80 | 900
29 | DSK | DPHE-FSL-S-1297 | 25/02/2025 | 12 | IOM | FSTP-12-02 | IOM-DEWATS-2020-09,C-12-002 | A | G-9 | DEWATS | 18.6 | 21.1787 | 92.154 | Effluent | 8.71 | 24.7 | 772 | 32.4 | 42.8 | 288 | 473 | 100 | 100 | 150 | 1.03% | 120 | 2870
30 | DSK | DPHE-FSL-S-1298 | 25/02/2025 | 5 | UNHCR | FSTP-05-02 | NGOF-C-5-ABR-02 | E | E-3 | ABR | 50 | 21.2013 | 92.15 | Effluent | 9.11 | 27 | 254 | 41.7 | 27.8 | 305 | 823 | 700 | 32700 | 140 | 2.25% | 296 | 1040
31 | DPHE | DPHE-FSL-S-1299 | 25/02/2025 | 4 Ext | ADB | FSTP-04-03 | Omni-1 | B | B-2 | Omni Processor | 180 | 21.2096 | 92.135 | Effluent | 7.48 | 28.2 | 378 | 23.2 | 26.6 | 115 | 308 | 2400 | 44400 | 166.66 | 0.61% | 920 | 900
32 | NGOF | DPHE-FSL-S-1300 | 2025-02-03 | 9 | IOM | FSTP-09-02 | IOM-DLT-2017-06-BMS-001 | F | C-9 | SSU | 6 | 21.1894 | 92.1603 | Effluent | 8.71 | 23.1 | 645 | 30.9 | 63 | 456 | 1261 | 0 | 4300 | 250 | 2.22% | 1120 | 3280
33 | NGOF | DPHE-FSL-S-1301 | 2025-02-03 | 9 | IOM | FSTP-09-03 | ABR-01 | F | C-9 | ABR | 30 | 21.1894 | 92.1603 | Effluent | 8.27 | 24.9 | 852 | 53.6 | 110.6 | 285 | 2089 | 2100 | 23600 | 1000 | 3.23% | 440 | 3230
34 | NGOF | DPHE-FSL-S-1302 | 2025-02-03 | 9 | IOM | FSTP-09-06 | IOM-DLT-2017-06-BMS-002 | A | B-1 | SSU | 6 | 21.1921 | 92.1604 | Effluent | 8.46 | 24.7 | 861 | 35.8 | 90 | 336 | 1379 | 0 | 200 | 352.94 | 0.14% | 440 | 3770
35 | NGOF | DPHE-FSL-S-1303 | 2025-02-03 | 9 | IOM | FSTP-09-07 | IOM-DEWATS-2019-10-C09-001 | A | B-2 | DEWATS | 15 | 21.1924 | 92.1596 | Effluent | 8 | 29.1 | 281 | 40.5 | 127 | 317 | 1250 | 0 | 100 | 266.66 | 0.32% | 200 | 5240
36 | NGOF | DPHE-FSL-S-1304 | 2025-02-03 | 9 | IOM | FSTP-09-08 | IOM-DEWATS-2021-07-C09-002 | B | I-2 | DEWATS | 18 | 21.1926 | 92.1584 | Effluent | 7.76 | 31.8 | 1260 | 37.6 | 141.2 | 247 | 1306 | 0 | 200 | 250 | 3.33% | 360 | 5290
37 | NGOF | DPHE-FSL-S-1305 | 2025-02-03 | 9 | IOM | FSTP-09-09 | IOM-DLT-2017-06-BMS-003 | C | H-20 | SSU | 6 | 21.1922 | 92.1572 | Effluent | 8.81 | 26.6 | 690 | 12.67 | 21.54 | 235 | 1252 | 0 | 40600 | 100 | 5.12% | 120 | 3050
38 | NGOF | DPHE-FSL-S-1306 | 2025-02-03 | 6 | UNICEF | FSTP-06-02 | ABR-FSM-02 | B | B-12 | ABR | 90 | 21.2043 | 92.1585 | Effluent | 8.47 | 27.2 | 1020 | 26 | 106 | 270 | 1144 | 700 | 1500 | 50 | 0.49% | 40 | 4080
39 | NGOF | DPHE-FSL-S-1307 | 2025-02-03 | 6 | UNICEF | FSTP-06-01 | ABR-FSM-01 | D | D-2 | ABR | 90 | 21.2018 | 92.1582 | Effluent | 8.74 | 26.9 | 1010 | 63.7 | 107.2 | 183 | 1028 | 0 | 200 | 233.33 | 3.08% | 360 | 4020
40 | NGOF | DPHE-FSL-S-1308 | 2025-02-03 | 6 | UNICEF | FSTP-06-04 | ABR-FSM-03 | C | C-3 | ABR | 90 | 21.2037 | 92.1561 | Effluent | 9.07 | 26.6 | 174 | 23.5 | 67 | 151 | 1113 | 2100 | 9600 | 200 | 4.47% | 240 | 3630
41 | NGOF | DPHE-FSL-S-1309 | 2025-02-03 | 6 | UNICEF | FSTP-06-03 | ABR-FSM-04 | A | A-2 | ABR | 90 | 21.2064 | 92.1563 | Effluent | 8.74 | 28 | 858 | 60.8 | 89.6 | 110 | 1066 | 1500 | 5600 | 200 | 2.51% | 40 | 3570
42 | NGOF | DPHE-FSL-S-1310 | 2025-02-03 | 4 Ext | UNHCR | FSTP-04-01 | FSTP-01 |  |  | Anarobic Legone | 700 | 21.2129 | 92.1391 | Effluent | 8.69 | 26.5 | 584 | 182 | 23.4 | 126 | 545 | 1100 | 27500 | 50 | 5.5% | 720 | 2210
43 | WVI | DPHE-FSL-S-1311 | 2025-03-03 | 8E | UNICEF | FSTP-08-02 | ABR-4 | B | B-60 | ABR | 50 | 21.1965 | 92.1614 | Effluent | 8.69 | 26.3 | 195 | 11.4 | 3.92 | 396 | 748 | 200 | 1100 | 250 | 2.05% | 352 | 3400
44 | WVI | DPHE-FSL-S-1312 | 2025-03-03 | 8E | UNICEF | FSTP-08-03 | UFF-03 | B | B-42 | UFF | 25 | 21.1998 | 92.1602 | Effluent | 8.1 | 27.2 | 302 | 29.8 | 15.28 | 119 | 1442 | 0 | 3900 | 200 | 1.99% | 640 | 3400
45 | WVI | DPHE-FSL-S-1313 | 2025-03-03 | 8E | UNICEF | FSTP-08-05 | WSP-02 | E | B-86 | WSP | 25 | 21.1985 | 92.1643 | Effluent | 8.53 | 25.5 | 350.7 | 24.5 | 9.02 | 106 | 258 | 200 | 19500 | 40 | 1.2% | 200 | 1250
46 | WVI | DPHE-FSL-S-1314 | 2025-03-03 | 8E | UNICEF | FSTP-08-01 | C-8E-C-B-65-01 | C | B-65 | WSP | 25 | 21.1948 | 92.1633 | Effluent | 8.05 | 25.9 | 401 | 17 | 24.6 | 226 | 1090 | 200 | 1100 | 200 | 2.21% | 520 | 4450
47 | WVI | DPHE-FSL-S-1315 | 2025-03-03 | 8E | UNICEF | FSTP-08-04 | ABR-08 | F | B-37 | ABR | 30 | 21.1975 | 92.1626 | Effluent | 8.19 | 29.3 | 101 | 24 | 9.3 | 301 | 856 | 900 | 7500 | 150 | 2.03% | 1080 | 3910
48 | WVI | DPHE-FSL-S-1316 | 2025-03-03 | 8E | UNICEF | FSTP-08-07 | UFF-06 | F | B-53 | UFF | 15 | 21.1975 | 92.1656 | Effluent | 8.84 | 26.8 | 365 | 15.6 | 0.22 | 212 | 881 | 0 | 11600 | 550 | 1.82% | 640 | 2630
49 | WVI | DPHE-FSL-S-1317 | 2025-03-03 | 8E | UNICEF | FSTP-08-06 | ABR-07 | D | B-70 | ABR | 50 | 21.1984 | 92.1668 | Effluent | 8.49 | 24.9 | 321 | 14.6 | 1.6 | 146 | 801 | 400 | 11300 | 100 | 1.4% | 40 | 2270
50 | BRAC | DPHE-FSL-S-1318 | 2025-04-03 | 10 | IOM | FSTP-10-07 | DEWATS-01 | E | F-40 | DEWATS | 18 | 21.1877 | 92.1517 | Effluent | 8.17 | 25.9 | 250.1 | 12 | 0.432 | 102 | 496 | 0 | 1100 | 50 | 2.43% | 400 | 3710
51 | BRAC | DPHE-FSL-S-1319 | 2025-04-03 | 10 | IOM | FSTP-10-05 | DEWATS-05 | F | G-6 | DEWATS | 12 | 21.1871 | 92.1576 | Effluent | 7.8 | 25.8 | 211.5 | 20.6 | 13.41 | 42 | 161 | 0 | 700 | 20 | 2.39% | 160 | 1810
52 | BRAC | DPHE-FSL-S-1320 | 2025-04-03 | 10 | IOM | FSTP-10-06 | IOM-23-01-C-03 | C | G-41 | DEWATS | 12 | 21.19 | 92.1546 | Effluent | 7.83 | 27.5 | 241.6 | 33.5 | 15.78 | 311 | 881 | 300 | 1700 | 250 | 0.8% | 840 | 3430
53 | BGS | DPHE-FSL-S-1321 | 2025-04-03 | 10 | IOM | FSTP-10-01 | L-004 | B | H-37 | LSP | 19 | 21.1944 | 92.1531 | Effluent | 9.25 | 28 | 381.9 | 18 | 11.32 | 406 | 1219 | 1600 | 4700 | 100 | 1.8% | 2320 | 3120
54 | WVI | DPHE-FSL-S-1322 | 2025-04-03 | 10 | IOM | FSTP-10-03 | D-001 | A | H-25 | DEWATS | 12 | 21.1927 | 92.1534 | Effluent | 8.19 | 29.3 | 260 | 20.3 | 1.22 | 339 | 1284 | 900 | 1700 | 1400 | 2.41% | 2000 | 4520
55 | WVI | DPHE-FSL-S-1323 | 2025-04-03 | 10 | IOM | FSTP-10-02 | IOM-DE-23-02-04 | A | A-27 | DEWATS | 12 | 21.1914 | 92.1562 | Effluent | 7.95 | 27.4 | 245 | 32.9 | 21.2 | 196 | 677 | 0 | 2300 | 50 | 1.6% | 240 | 3820
56 | DPHE/ ADB | DPHE-FSL-S-1324 | 2025-04-03 | 13 | ADB | FSTP-13-11 | W9-B | F | F-5 | Biological Process | 50 | 21.1832 | 92.1371 | Effluent | 8.84 | 31.4 | 165 | 29.8 | 6.2 | 216 | 723 | 700 | 3700 | 155.55 | 2.43% | 600 | 2300
57 | VERC | DPHE-FSL-S-1325 | 2025-09-03 | 8W | UNICEF | FSTP-08-11 | FSM-01 | B | A-16 | ABR | 60 | 21.1957 | 92.1577 | Effluent | 8.18 | 25.8 | 279 | 42.1 | 28.6 | 119 | 295 | 8700 | 48700 | 20 | 0.86% | 720 | 1260
58 | VERC | DPHE-FSL-S-1326 | 2025-09-03 | 8W | UNICEF | FSTP-08-13 | FSM-01 | D | A-39 | ABR | 30 | 21.199 | 92.1558 | Effluent | 8.2 | 25.6 | 139 | 3.26 | 15.2 | 51 | 238 | 150700 | 159700 | 80 | 0.78% | 280 | 680
59 | VERC | DPHE-FSL-S-1327 | 2025-09-03 | 8W | UNICEF | FSTP-08-14 | FSM-01 | D | I-20 | UFF | 10 | 21.1981 | 92.155 | Effluent | 8.07 | 25.6 | 293 | 56.8 | 23.6 | 65 | 427 | 65000 | 66000 | 177.77 | 1.1% | 160 | 1270
60 | VERC | DPHE-FSL-S-1328 | 2025-09-03 | 8W | UNICEF | FSTP-08-20 | FSM-01 | F | A-65 | ABR | 60 | 21.1967 | 92.1521 | Effluent | 7.98 | 24.1 | 203 | 34.9 | 9.31 | 76 | 227 | 1400 | 51400 | 80 | 1.48% | 1400 | 1160
61 | VERC | DPHE-FSL-S-1329 | 2025-09-03 | 8W | UNICEF | FSTP-08-09 | FSM-01 | A | A-19 | UFF | 15 | 21.1978 | 92.1601 | Effluent | 8.35 | 22.8 | 488 | 47.8 | 46 | 262 | 789 | 76800 | 78100 | 166.66 | 3.26% | 640 | 2490
62 | VERC | DPHE-FSL-S-1330 | 2025-09-03 | 8W | UNICEF | FSTP-08-10 | FSM-01 | A | A-28 | UFF | 15 | 21.1986 | 92.1584 | Effluent | 7.35 | 24.4 | 244 | 4.42 | 47.1 | 114 | 303 | 120300 | 127500 | 20 | 1.42% | 160 | 1180
63 | VERC | DPHE-FSL-S-1331 | 2025-10-03 | 8W | UNICEF | FSTP-08-15 | FSM-01 | E | A-49 | UFF | 15 | 21.1992 | 92.154 | Effluent | 7.92 | 26.4 | 109 | 13.5 | 2.5 | 90 | 176 | 59200 | 67900 | 20 | 1.21% | 200 | 860
64 | VERC | DPHE-FSL-S-1332 | 2025-10-03 | 8W | UNICEF | FSTP-08-20 | FSM-01 | F | A-61 | UFF | 10 | 21.1954 | 92.1537 | Effluent | 8.77 | 25.9 | 916 | 30.4 | 49 | 226 | 1124 | 0 | 0 | 300 | 3.67% | 40 | 3650
65 | VERC | DPHE-FSL-S-1333 | 2025-10-03 | 8W | UNICEF | FSTP-08-16 | FSM-01 | E | A-66 | WSP | 10 | 21.1984 | 92.1509 | Effluent | 7.42 | 27.7 | 50.3 | 5.83 | 1.33 | 44 | 120 | 100 | 3300 | 10 | 0.79% | 240 | 260
66 | VERC | DPHE-FSL-S-1334 | 2025-10-03 | 8W | UNICEF | FSTP-08-19 | FSM-01 | E | A-55 | WSP | 10 | 21.2004 | 92.1518 | Effluent | 7.92 | 27.9 | 164 | 41.5 | 0.12 | 68 | 140 | 4500 | 18900 | 10 | 7.02% | 40 | 320
67 | ACF | DPHE-FSL-S-1335 | 2025-11-03 | 11 | IOM | FSTP-11-05 | DEWATS-02 | A | A-3 | DEWATS | 18 | 21.1834 | 92.1582 | Effluent | 7.95 | 26.7 | 669 | 27.2 | 51.1 | 217 | 724 | 1000 | 51500 | 160 | 4.46% | 80 | 4510
68 | ACF | DPHE-FSL-S-1336 | 2025-11-03 | 11 | IOM | FSTP-11-06 | DEWATS-03 | D | D-7 | DEWATS | 10 | 21.1856 | 92.1566 | Effluent | 8.27 | 27.2 | 838 | 13.5 | 46.4 | 111 | 508 | 5600 | 9700 | 20 | 3.22% | 120 | 3530
69 | ACF | DPHE-FSL-S-1337 | 2025-11-03 | 11 | IOM | FSTP-11-02 | DEWATS-04 | A | A-14 | DEWATS | 15 | 21.1827 | 92.1552 | Effluent | 8.86 | 24.8 | 546 | 55.3 | 55.3 | 135 | 305 | 0 | 200 | 20 | 0.59% | 280 | 2540
70 | ACF | DPHE-FSL-S-1338 | 2025-11-03 | 11 | IOM | FSTP-11-04 | DEWATS-01 | A | A-2 | DEWATS | 18 | 21.1821 | 92.1573 | Effluent | 7.37 | 26 | 843 | 17.4 | 52.6 | 240 | 620 | 900 | 78600 | 120 | 0.4% | 240 | 3820
71 | NRC | DPHE-FSL-S-1339 | 2025-11-03 | 19 | IOM | FSTP-19-02 | IOM-DEWATS-2022-11-C-19-001 | A | A-1 | DEWATS | 15 | 21.1853 | 92.1407 | Effluent | 8.65 | 29.5 | 509 | 21.5 | 61.9 | 253 | 593 | 0 | 2900 | 100 | 2.62% | 2400 | 2050
72 | NRC | DPHE-FSL-S-1340 | 2025-11-03 | 19 | IOM | FSTP-19-03 | IOM-DEWATS-2022-11-C-19-002 | A | A-1 | DEWATS | 15 | 21.1853 | 92.1406 | Effluent | 6.32 | 28.1 | 920 | 18.9 | 133 | 230 | 623 | 200 | 38600 | 10 | 3.2% | 520 | 2020
73 | BDRCS | DPHE-FSL-S-1341 | 2025-11-03 | 19 | IOM | FSTP-19-01 | BDRCS-FSTP-C19-01 | D | D-13 | ABR | 75 | 21.1806 | 92.1475 | Effluent | 8.36 | 28.5 | 725 | 19.9 | 55.4 | 272 | 726 | 0 | 2800 | 160 | 3.03% | 1840 | 1630
74 | DSK | DPHE-FSL-S-1342 | 2025-11-03 | 5 | UNHCR | FSTP-05-03 | NGOF-C-5-ABR-01 | E | E-7 | ABR | 50 | 21.1992 | 92.148 | Effluent | 6.15 | 34.2 | 462 | 11.6 | 3 | 201 | 291 | 1700 | 39500 | 50 | 12.05% | 120 | 4340
75 | BDRCS | DPHE-FSL-S-1343 | 16/03/2025 | 18 | IOM | FSTP-18-01 | FSM-C18-2 | M | M-19 | ABR | 75 | 21.1878 | 92.1441 | Effluent | 7.81 | 26.8 | 466 | 17.8 | 33.2 | 179 | 691 | 100 | 100 | 40 | 3.19% | 240 | 1960
76 | DSK | DPHE-FSL-S-1344 | 16/03/2025 | 18 | IOM | FSTP-18-05 | DEWATS-01 | C | K-9 | DEWATS | 18 | 21.1876 | 92.1516 | Effluent | 7.68 | 28.9 | 710 | 77.2 | 3.44 | 204 | 628 | 0 | 0 | 30 | 1.68% | 320 | 2200
77 | DSK | DPHE-FSL-S-1345 | 16/03/2025 | 18 | IOM | FSTP-18-12 | IOM-DEWATS-2023-06-C18-002 | A | A-1(H-64) | DEWATS | 18 | 21.1946 | 92.1461 | Effluent | 8.57 | 28.9 | 864 | 12.3 | 54.6 | 204 | 786 | 0 | 5700 | 62.5 | 1.93% | 1040 | 2910
78 | DSK | DPHE-FSL-S-1346 | 16/03/2025 | 18 | IOM | FSTP-18-08 | IOM-DEWATS-2023-06-C18-004 | C | G-43 | DEWATS | 18 | 21.1922 | 92.1476 | Effluent | 7.59 | 29.6 | 956 | 26.7 | 30 | 213 | 873 | 0 | 2700 | 166.66 | 1.69% | 1120 | 3990
79 | DSK | DPHE-FSL-S-1347 | 16/03/2025 | 18 | IOM | FSTP-18-09 | IOM-DEWATS-2023-06-C18-005 | A | A-2(H-62) | DEWATS | 18 | 21.1924 | 92.1479 | Effluent | 8.24 | 28.8 | 924 | 22.4 | 5.6 | 189 | 957 | 0 | 10500 | 133.33 | 3% | 480 | 3350
80 | DSK | DPHE-FSL-S-1348 | 16/03/2025 | 18 | IOM | FSTP-18-11 | IOM-DEWATS-2023-06-C18-003 | B | H-61 | DEWATS | 18 | 21.1904 | 92.1459 | Effluent | 8.04 | 26 | 826 | 70.7 | 1.26 | 171 | 774 | 0 | 3300 | 80 | 1.63% | 1560 | 2220
81 | WVI | DPHE-FSL-S-1349 | 17/03/2025 | 13 | IOM | FSTP-13-10 | WSP-02 | A | A-6 | WSP | 25 | 21.1769 | 92.1419 | Effluent | 7.7 | 26.5 | 512 | 14.4 | 7.12 | 196 | 494 | 300 | 33600 | 100 | 2.94% | 200 | 1980
82 | SHED | DPHE-FSL-S-1350 | 17/03/2025 | 13 | IOM | FSTP-13-09 | IOM-DEWATS-22-06-C-13-0013 | C | C-1 | DEWATS | 18 | 21.1771 | 92.141 | Effluent | 7.82 | 28.7 | 586 | 53.5 | 5.84 | 200 | 258 | 14100 | 19700 | 10 | 1.98% | 240 | 2010
83 | SHED | DPHE-FSL-S-1351 | 17/03/2025 | 13 | IOM | FSTP-13-07 | IOM-DEWATS-2020-09-001 | E | E-1 | DEWATS | 18 | 21.1775 | 92.1365 | Effluent | 7.73 | 28.3 | 836 | 16.5 | 37.4 | 233 | 631 | 0 | 0 | 200 | 2.72% | 160 | 3140
84 | SHED | DPHE-FSL-S-1352 | 17/03/2025 | 13 | IOM | FSTP-13-08 | IOM-DEWATS-2020-09-002 | E | E-1 | DEWATS | 18 | 21.1776 | 92.1365 | Effluent | 7.69 | 28.4 | 830 | 22.7 | 40.4 | 205 | 531 | 0 | 8700 | 80 | 2.97% | 240 | 2640
85 | SHED | DPHE-FSL-S-1353 | 17/03/2025 | 13 | IOM | FSTP-13-01 | WVI-003 | E | E-1 | WSP | 25 | 21.1776 | 92.1366 | Effluent | 8.42 | 29.5 | 610 | 11 | 52 | 244 | 459 | 500 | 6100 | 40 | 1.99% | 640 | 1780
86 | BDRCS | DPHE-FSL-S-1354 | 17/03/2025 | 13 | IOM | FSTP-13-02 | PA-FSTP-01 | G | G-1 | UFF | 25 | 21.1719 | 92.1344 | Effluent | 8.19 | 27.7 | 842 | 15.4 | 75 | 177 | 612 | 3100 | 14500 | 140 | 4.27% | 80 | 2480
87 | BDRCS | DPHE-FSL-S-1355 | 17/03/2025 | 13 | IOM | FSTP-13-03 | PA-FSTP-02 | G | G-3 | UFF | 25 | 21.1817 | 92.1364 | Effluent | 8.42 | 31.2 | 712 | 15.2 | 70.2 | 216 | 905 | 0 | 0 | 140 | 3.99% | 440 | 3230
88 | NRC | DPHE-FSL-S-1356 | 17/03/2025 | 13 | IOM | FSTP-13-05 | NRC- UFF-04 | F | F-4 | UFF | 25 | 21.1808 | 92.1375 | Effluent | 8.56 | 29.3 | 1112 | 16.7 | 29.8 | 203 | 1116 | 0 | 0 | 300 | 3.79% | 960 | 3650
89 | NRC | DPHE-FSL-S-1357 | 17/03/2025 | 13 | IOM | FSTP-13-06 | IOM-DEWATS-2022-08-C13-004 | F | F-2 | DEWATS | 6 | 21.1819 | 92.1404 | Effluent | 8.25 | 28.3 | 820 | 16.9 | 32 | 196 | 673 | 0 | 0 | 250 | 3.21% | 840 | 3770
90 | DSK | DPHE-FSL-S-1358 | 18/03/2025 | 16 | UNICEF | FSTP-16-07 | DSKIVY-16-ABR-004-2020 | C | C-5 | ABR | 35 | 21.1536 | 92.152 | Effluent | 8.75 | 25 | 468 | 141 | 15.28 | 209 | 904 | 0 | 29600 | 250 | 3.73% | 1560 | 2830
91 | DSK | DPHE-FSL-S-1359 | 18/03/2025 | 16 | UNICEF | FSTP-16-05 | DSK-BRAC-EKN-16-ABR-03/19 | C | C-1 | ABR | 35 | 21.1539 | 92.1518 | Effluent | 8.75 | 27.2 | 1408 | 15.7 | 19.88 | 218 | 770 | 0 | 30600 | 150 | 4.27% | 320 | 3340
92 | DSK | DPHE-FSL-S-1360 | 18/03/2025 | 16 | UNICEF | FSTP-16-02 | DSK-Unicef-16-UFF-002/2020 | A | A-5 | UFF | 10 | 21.1596 | 92.1516 | Effluent | 8.53 | 28 | 708 | 17.1 | 90.6 | 231 | 1359 | 300 | 27900 | 450 | 3.65% | 1320 | 3230
93 | DSK | DPHE-FSL-S-1361 | 18/03/2025 | 16 | UNICEF | FSTP-16-04 | C-16-D-08-ABR-007 | D | D-8 | ABR | 30 | 21.1542 | 92.145 | Effluent | 8.35 | 29.5 | 1324 | 13.5 | 34.8 | 179 | 554 | 700 | 4700 | 60 | 2.01% | 120 | 3210
94 | DSK | DPHE-FSL-S-1362 | 18/03/2025 | 16 | UNICEF | FSTP-16-06 | C-16-D-02-UFF-006 | D | D-2 | UFF | 10 | 21.1522 | 92.1501 | Effluent | 8.11 | 29.6 | 912 | 18.4 | 89.6 | 356 | 1613 | 1900 | 4500 | 600 | 4.51% | 1960 | 2280
95 | DSK | DPHE-FSL-S-1363 | 18/03/2025 | 16 | UNICEF | FSTP-16-01 | C-16-B-02-ABR-002 | B | B-4 | ABR | 35 | 21.1565 | 92.1493 | Effluent | 8.15 | 30 | 936 | 20.9 | 81.2 | 406 | 1820 | 0 | 12600 | 666.66 | 3.74% | 1280 | 2950
96 | DSK | DPHE-FSL-S-1364 | 18/03/2025 | 16 | UNICEF | FSTP-16-03 | DSK-Unicef-16-ABR-001/2019 | A | A-2 | ABR | 30 | 21.1582 | 92.1488 | Effluent | 8.75 | 29.5 | 750 | 20.7 | 114.2 | 476 | 1796 | 0 | 400 | 700 | 3.36% | 2000 | 3130
97 | BRAC | DPHE-FSL-S-1365 | 18/03/2025 | 21 | UNHCR | FSTP-21-02 | C-21-ABR-Omani | C | Omani Play Ground | ABR | 60 | 21.1318 | 92.1608 | Effluent | 8.45 | 34.5 | 714 | 18.3 | 60.8 | 391 | 1392 | 400 | 1000 | 500 | 3.45% | 1000 | 3080
98 | NGOF | DPHE-FSL-S-1366 | 2025-07-04 | 9 | IOM | FSTP-09-01 | IOM-DEWATS-2021-11-C-9-004 | F | G-3 | DEWATS | 18 | 21.1893 | 92.1589 | Effluent | 8.17 | 30.8 | 985 | 19.5 | 44 | 136 | 739 | 0 | 0 | 250 | 5.2% | 320 | 4450
99 | NGOF | DPHE-FSL-S-1367 | 2025-07-04 | 9 | IOM | FSTP-09-04 | IOM-DEWATS-2021-07-C09-003 | F | C-17 | DEWATS | 18 | 21.188 | 92.1604 | Effluent | 7.77 | 26.2 | 644 | 23.5 | 43.9 | 90 | 340 | 3600 | 36000 | 100 | 4.1% | 40 | 2930
100 | DSK | DPHE-FSL-S-1368 | 2025-07-04 | 22 | UNICEF | FSTP-22-01 | DSK-UNICEF-22-ABR-01/2020 | A | A-1 | ABR | 50 | 21.0878 | 92.2006 | Effluent | 8.07 | 30.1 | 1010 | 14.4 | 38 | 190 | 1104 | 100 | 400 | 300 | 4.78% | 40 | 3200
101 | DSK | DPHE-FSL-S-1369 | 2025-07-04 | 22 | UNICEF | FSTP-22-03 | DSK-UNICEF-22-ABR-03/2021 | C | C-3 | ABR | 60 | 21.0876 | 92.1936 | Effluent | 8.2 | 30.3 | 1020 | 14.2 | 48.2 | 180 | 1021 | 100 | 100 | 300 | 4.78% | 880 | 2900
102 | DSK | DPHE-FSL-S-1370 | 2025-07-04 | 22 | UNICEF | FSTP-22-02 | DSK-UNICEF-22-ABR-02/2020 | C | C-3 | ABR | 60 | 21.0876 | 92.1938 | Effluent | 8.69 | 31.2 | 901 | 15 | 48.5 | 137 | 877 | 0 | 2900 | 250 | 5.39% | 40 | 2300
103 | DSK | DPHE-FSL-S-1371 | 2025-09-04 | 24 | IOM | FSTP-24-01 | FSM-Capm-24-01 | E | E-5 | DEWATS | 18 | 21.975 | 92.2423 | Effluent | 9.15 | 30.8 | 351 | 11.3 | 21.9 | 44 | 378 | 7900 | 19600 | 125 | 4.55% | 40 | 2270
104 | DSK | DPHE-FSL-S-1372 | 2025-09-04 | 24 | IOM | FSTP-24-03 | DEWATS-03 | E | E-5 | DEWATS | 15 | 21.9712 | 92.2435 | Effluent | 9.06 | 30.1 | 449 | 9.71 | 22.5 | 71 | 473 | 0 | 1900 | 150 | 4.55% | 40 | 2610
105 | DSK | DPHE-FSL-S-1373 | 2025-09-04 | 24 | IOM | FSTP-24-02 | DEWATS-Unit-04 | D | D-2 | DEWATS | 40 | 20.9751 | 92.2424 | Effluent | 8.05 | 29.4 | 113 | 2.11 | 8.57 | 45 | 170 | 23600 | 53900 | 40 | 0.9% | 80 | 300
106 | DSK | DPHE-FSL-S-1374 | 2025-09-04 | 24 | IOM | FSTP-24-06 | IOM-DEWATS-2023-01-C-24-002 | D | D-3 | DEWATS | 6 | 20.9695 | 92.2433 | Effluent | 8.85 | 30.8 | 742 | 15.4 | 38.7 | 139 | 1232 | 200 | 3800 | 300 | 4.59% | 1240 | 3860
107 | ANANDA | DPHE-FSL-S-1375 | 2025-09-04 | 24 | IOM | FSTP-24-04 | IOM-DEWATS-01 | B | B-4 | DEWATS | 18 | 20.9551 | 92.2424 | Effluent | 8.38 | 31.2 | 311 | 26.8 | 65.1 | 145 | 659 | 0 | 0 | 25 | 4.78% | 80 | 1610
108 | ANANDA | DPHE-FSL-S-1376 | 2025-09-04 | 24 | IOM | FSTP-24-05 | IOM-DEWATS-02 | B | B-4 | DEWATS | 18 | 20.9551 | 92.2424 | Effluent | 9.2 | 32.8 | 989 | 23.9 | 37.4 | 170 | 970 | 0 | 0 | 50 | 3.84% | 600 | 3740
109 | SCI | DPHE-FSL-S-1377 | 2025-09-04 | 25 | IOM | FSTP-25-01 | SCI-C25-Alikhali-DEWATS-FSTP-02 | D | D-9 | DEWATS | 30 | 20.9785 | 92.2426 | Effluent | 8.7 | 31.2 | 856 | 14.6 | 44.4 | 118 | 681 | 1100 | 3500 | 133.33 | 3.47% | 40 | 2250
110 | BRAC | DPHE-FSL-S-1378 | 2025-09-04 | 25 | IOM | FSTP-25-02 | C-25-B-1-FSTP-001 | B | B-1 | ABR | 30 | 21.144 | 92.1946 | Effluent | 9.19 | 30.3 | 1240 | 25.1 | 43.1 | 212 | 1688 | 500 | 4600 | 450 | 5.72% | 40 | 4220
111 | SHED | DPHE-FSL-S-1379 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -13 | IOM-DLT-001(KSR-19) | S-1 | B-4 | SSU | 16 | 21.1868 | 92.1359 | Effluent | 8.78 | 28.6 | 202 | 14.1 | 11.8 | 412 | 446 | 10500 | 18700 | 40 | 1.04% | 240 | 1460
112 | SHED | DPHE-FSL-S-1380 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -15 | IOM-DLT-002(KSR-29) | S-3 | B-5 | SSU | 16 | 21.1909 | 92.1342 | Effluent | 8.94 | 31.2 | 484 | 21.4 | 59.9 | 330 | 924 | 3800 | 17500 | 125 | 0.83% | 40 | 2130
113 | SHED | DPHE-FSL-S-1381 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -19 | IOM-DLT-005(KSR-23) | S-3 | B-4 | SSU | 16 | 21.1984 | 92.1359 | Effluent | 8.98 | 31.1 | 413 | 117.1 | 15 | 315 | 1350 | 1900 | 36000 | 133.33 | 0.91% | 160 | 2290
114 | SHED | DPHE-FSL-S-1382 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -16 | IOM-DEWATS-2023-06-C-20Ext-002 | S-2 | B-1 | DEWATS | 20 | 21.1918 | 92.134 | Effluent | 7.21 | 31.9 | 291 | 22.9 | 13.9 | 491 | 360 | 200 | 17500 | 70 | 1.01% | 80 | 1810
115 | SHED | DPHE-FSL-S-1383 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -09 | IOM-DLT-003(KSR-21) | S-3 | B-4 | DEWATS | 16 | 21.1916 | 92.1331 | Effluent | 7.7 | 29.8 | 1010 | 14.8 | 53.5 | 156 | 913 | 0 | 0 | 200 | 2.25% | 200 | 4180
116 | SHED | DPHE-FSL-S-1384 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -12 | IOM-DLT-008(KSR-26) | S-3 | B-1 | SSU | 16 | 21.1945 | 92.1339 | Effluent | 8.66 | 29.8 | 571 | 14.6 | 29.6 | 41 | 1293 | 0 | 81100 | 150 | 0.82% | 120 | 2600
117 | SHED | DPHE-FSL-S-1385 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -08 | IOM-DLT-005(KSR-24) | S-3 | B-3 | DEWATS | 16 | 21.1943 | 92.1321 | Effluent | 9.09 | 30.2 | 581 | 30.3 | 3.99 | 316 | 550 | 0 | 0 | 57.14 | 1.42% | 760 | 1270
118 | SHED | DPHE-FSL-S-1386 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -20 | IOM-DLT-009(KSR-27) | S-2 | B-5 | DEWATS | 16 | 21.1945 | 92.1335 | Effluent | 6.83 | 29.4 | 63.9 | 39 | 2.44 | 286 | 129 | 2500 | 7500 | 10 | 0.41% | 200 | 940
119 | SHED | DPHE-FSL-S-1387 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -11 | IOM-DLT-10(KSR-28) | S-4 | B-7 | SSU | 16 | 21.1984 | 92.1359 | Effluent | 9.04 | 30.8 | 580 | 15.9 | 36.5 | 236 | 1067 | 3100 | 29600 | 166.66 | 2.44% | 280 | 2960
120 | SHED | DPHE-FSL-S-1388 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -14 | IOM-DLT-004(KSR-15) | S-2 | B-2 | DEWATS | 16 | 21.1944 | 92.1365 | Effluent | 9.02 | 31.7 | 180 | 35.3 | 26.8 | 319 | 574 | 0 | 5100 | 40 | 0.81% | 120 | 1800
121 | SHED | DPHE-FSL-S-1389 | 15/04/2025 | 20 Ext | IOM | FSTP-20 -23 | IOM-DLT-015(KSR-30) | S | B-2 | SSU | 15 | 21.1935 | 92.137 | Effluent | 8.95 | 29.3 | 421 | 7.05 | 60.5 | 506 | 519 | 11900 | 59700 | 166.66 | 1% | 120 | 2830
122 | SHED | DPHE-FSL-S-1390 | 15/04/2025 | 20 | IOM | FSTP-20 -16 | IOM-DLT-004(KSR-14) | A | M-35 | DEWATS | 18 | 21.192 | 92.1414 | Effluent | 8.17 | 29.5 | 781 | 11.2 | 5.25 | 175 | 465 | 0 | 0 | 100 | 1.21% | 80 | 2300
123 | SHED | DPHE-FSL-S-1391 | 15/04/2025 | 20 | IOM | FSTP-20 -04 | IOM-DLT-008(KSR-18) | B | M-31 | SSU | 20 | 21.1912 | 92.1385 | Effluent | 7.95 | 29.6 | 703 | 17.2 | 50.4 | 128 | 1266 | 0 | 0 | 433.33 | 2.44% | 120 | 2240
124 | SHED | DPHE-FSL-S-1392 | 15/04/2025 | 20 | IOM | FSTP-20 -05 | IOM-DLT-003(KSR-13) | A | M-30 | DEWATS | 18 | 21.1929 | 92.1435 | Effluent | 8.95 | 29.8 | 410 | 18.2 | 47.9 | 492 | 694 | 0 | 0 | 100 | 2.03% | 200 | 3050
125 | SHED | DPHE-FSL-S-1393 | 15/04/2025 | 20 | IOM | FSTP-20 -03 | IOM-DLT-006(KSR-16) | A | M-27 | SSU | 14 | 21.1909 | 92.1403 | Effluent | 8.15 | 28.8 | 755 | 8.35 | 37.1 | 39 | 381 | 0 | 0 | 20 | 1.2% | 360 | 2950
126 | SHED | DPHE-FSL-S-1394 | 15/04/2025 | 20 | IOM | FSTP-20 -02 | IOM-DLT-2018-10-C-20(KSR-11) | A | M-22 | SSU | 14 | 21.1935 | 92.1429 | Effluent | 8.29 | 29.3 | 657 | 20.2 | 51.1 | 117 | 1972 | 0 | 900 | 300 | 2.7% | 240 | 2120
127 | SCI | DPHE-FSL-S-1395 | 15/04/2025 | 20 | IOM | FSTP-20 -07 | SCI-FSTP-01 | B | M-24 | ABR | 20 | 21.1877 | 92.1407 | Effluent | 8.53 | 29.5 | 65.8 | 26.5 | 6.65 | 602 | 92.2 | 0 | 1100 | 30 | 1.83% | 160 | 2170
128 | SHED | DPHE-FSL-S-1396 | 15/04/2025 | 20 | IOM | FSTP-20-01 | IOM-DLT-007-KSR-17 | B | M-39 | SSU | 14 | 21.1888 | 92.1395 | Effluent | 8.19 | 30.3 | 153 | 8.47 | 47.2 | 326 | 248 | 2900 | 8700 | 20 | 0.81% | 200 | 2160
129 | CARE BANGLADESH | DPHE-FSL-S-1397 | 16/04/25 | 15 | UNICEF | FSTP-15-01 | UFF-01 | A | A-5 | UFF | 15 | 21.1621 | 92.1502 | Effluent | 8.08 | 27.6 | 936 | 27.5 | 62.3 | 489 | 1496 | 1100 | 12600 | 600 | 2.44% | 120 | 3380
130 | CARE BANGLADESH | DPHE-FSL-S-1398 | 16/04/25 | 15 | UNICEF | FSTP-15-02 | WSP-02 | A | A-8 | WSP | 35 | 21.1639 | 92.1496 | Effluent | 8.73 | 30.8 | 525 | 14.8 | 8.89 | 212 | 775 | 6500 | 19600 | 250 | 1.22% | 200 | 2950
131 | CARE BANGLADESH | DPHE-FSL-S-1399 | 16/04/25 | 15 | UNICEF | FSTP-15-03 | ABR-03 | B | B-2 | ABR | 35 | 21.1613 | 92.147 | Effluent | 8.79 | 31.7 | 836 | 20.2 | 71.7 | 281 | 1378 | 1700 | 16800 | 500 | 2.01% | 600 | 3250
132 | CARE BANGLADESH | DPHE-FSL-S-1400 | 16/04/25 | 15 | UNICEF | FSTP-15-19 | UFF-04 | C | C-4 | UFF | 15 | 21.1613 | 92.1445 | Effluent | 8.72 | 30.9 | 650 | 27 | 52.3 | 79 | 849 | 9500 | 3600 | 33.33 | 2.24% | 40 | 3100
133 | CARE BANGLADESH | DPHE-FSL-S-1401 | 16/04/25 | 15 | UNICEF | FSTP-15-04 | WSP-05 | C | C-10 | WSP | 35 | 21.1638 | 92.1443 | Effluent | 7.95 | 31 | 185 | 18.9 | 6.5 | 182 | 384 | 500 | 48500 | 50 | 1.21% | 320 | 3570
134 | CARE BANGLADESH | DPHE-FSL-S-1402 | 16/04/25 | 15 | UNICEF | FSTP-15-05 | UFF-06 | D | D-11 | UFF | 15 | 21.163 | 92.1435 | Effluent | 8.8 | 31.7 | 1060 | 32.1 | 83.7 | 394 | 1407 | 0 | 0 | 400 | 2.82% | 160 | 3500
135 | MSF-Hospital | DPHE-FSL-S-1403 | 16/04/25 | 15 | UNICEF | FSTP-15-23 |  | C | C-6 | DEWATS | 105 | 21.1611 | 92.1429 | Effluent | 7.85 | 29.7 | 82 | 1.86 | 20.2 | 133 | 209 | 116500 | 116500 | 80 | 0.43% | 80 | 1950
136 | CARE BANGLADESH | DPHE-FSL-S-1404 | 16/04/25 | 15 | UNICEF | FSTP-15-06 | UFF-07 | D | D-6 | UFF | 15 | 21.162 | 92.142 | Effluent | 8.2 | 31.9 | 521 | 10.2 | 46.3 | 357 | 843 | 89600 | 145600 | 333.33 | 1.63% | 40 | 3190
137 | CARE BANGLADESH | DPHE-FSL-S-1405 | 16/04/25 | 15 | UNICEF | FSTP-15-07 | UFF-10 | E | E-13 | UFF | 15 | 21.162 | 92.1401 | Effluent | 7.8 | 30.2 | 518 | 13.2 | 41.7 | 208 | 1040 | 12000 | 17000 | 100 | 2.05% | 160 | 2560
138 | CARE BANGLADESH | DPHE-FSL-S-1406 | 16/04/25 | 15 | UNICEF | FSTP-15-08 | UFF-08 | D | D-14 | UFF | 15 | 21.1619 | 92.1382 | Effluent | 8.2 | 30.3 | 565 | 10.6 | 72.5 | 133 | 1057 | 16000 | 50100 | 200 | 1% | 80 | 2950
139 | CARE BANGLADESH | DPHE-FSL-S-1407 | 16/04/25 | 15 | UNICEF | FSTP-15-17 | ABR-17 | G | G-8 | ABR | 35 | 21.1578 | 92.1466 | Effluent | 8.21 | 30.8 | 1010 | 19.8 | 56.4 | 1305 | 1611 | 900 | 14500 | 500 | 2.21% | 80 | 3090
140 | CARE BANGLADESH | DPHE-FSL-S-1408 | 16/04/25 | 15 | UNICEF | FSTP-15-22 | UFF-18 | G | G-10 | UFF | 15 | 21.1585 | 92.1472 | Effluent | 8.27 | 30.9 | 222 | 15.3 | 74.7 | 156 | 1087 | 7500 | 19500 | 50 | 1.2% | 80 | 3080
141 | CARE BANGLADESH | DPHE-FSL-S-1409 | 16/04/25 | 15 | UNICEF | FSTP-15-10 | UFF-13 | E | E-3 | UFF | 15 | 21.1585 | 92.1443 | Effluent | 8.36 | 30.6 | 956 | 21.4 | 45 | 352 | 1623 | 3500 | 12500 | 100 | 2.41% | 160 | 3070
142 | CARE BANGLADESH | DPHE-FSL-S-1410 | 16/04/25 | 15 | UNICEF | FSTP-15-20 | UFF-12 | E | E-8 | UFF | 15 | 21.1606 | 92.143 | Effluent | 8.9 | 30.9 | 419 | 7.3 | 28.7 | 135 | 456 | 4500 | 19600 | 60 | 1.44% | 200 | 3310
143 | CARE BANGLADESH | DPHE-FSL-S-1411 | 16/04/25 | 15 | UNICEF | FSTP-15-13 | ABR-14 | F | F-10 | ABR | 35 | 21.1509 | 92.1426 | Effluent | 8.3 | 30.3 | 992 | 21.7 | 63 | 160 | 1140 | 4900 | 19500 | 150 | 0.4% | 120 | 3090
144 | CARE BANGLADESH | DPHE-FSL-S-1412 | 16/04/25 | 15 | UNICEF | FSTP-15-12 | UFF-15 | F | F-7 | UFF | 15 | 21.1584 | 92.1419 | Effluent | 8.33 | 30.8 | 528 | 15.1 | 25.5 | 190 | 492 | 500 | 6500 | 80 | 1.45% | 200 | 2960
145 | CARE BANGLADESH | DPHE-FSL-S-1413 | 16/04/25 | 15 | UNICEF | FSTP-15-14 | UFF-16 | F | F-6 | UFF | 15 | 21.1568 | 92.1436 | Effluent | 8.2 | 30.7 | 372 | 16 | 26.9 | 440 | 1270 | 4100 | 14500 | 150 | 1.21% | 80 | 3080
146 | CARE BANGLADESH | DPHE-FSL-S-1414 | 16/04/25 | 15 | UNICEF | FSTP-15-21 | UFF-19 | H | H-4 | UFF | 15 | 21.1575 | 92.1402 | Effluent | 8.1 | 30.2 | 784 | 47.3 | 70.4 | 365 | 1610 | 6900 | 11100 | 66.66 | 1.22% | 320 | 3010
147 | CARE BANGLADESH | DPHE-FSL-S-1415 | 16/04/25 | 15 | UNICEF | FSTP-15-16 | WSP-22 | H | H-15 | WSP | 35 | 21.1627 | 92.1968 | Effluent | 8.37 | 29.9 | 611 | 23.6 | 43.9 | 156 | 1029 | 112000 | 126000 | 150 | 1.69% | 80 | 2970
148 | CARE BANGLADESH | DPHE-FSL-S-1416 | 16/04/25 | 15 | UNICEF | FSTP-15-11 | UFF-21 | H | H-9 | UFF | 15 | 21.1587 | 92.1372 | Effluent | 8.36 | 30.8 | 405 | 8.16 | 52.3 | 55 | 281 | 3600 | 14000 | 10 | 1% | 200 | 3010
149 | CARE BANGLADESH | DPHE-FSL-S-1417 | 16/04/25 | 15 | UNICEF | FSTP-15-09 | WSP-09 | E | E-16 | WSP | 35 | 21.1629 | 92.1368 | Effluent | 8.95 | 30.7 | 432 | 19.5 | 40.5 | 119 | 521 | 9600 | 20800 | 66.66 | 1% | 320 | 3250
150 | BRAC | DPHE-FSL-S-1418 | 20/04/25 | 14 | UNICEF | FSTP-14-06 | C-14-D-D2-FSM-07 | D | D-2 | ABR | 50 | 21.168 | 92.1424 | Effluent | 8.74 | 29.2 | 324 | 28 | 8.92 | 45 | 207 | 900 | 29600 | 100 | 1.44% | 200 | 1760
151 | BRAC | DPHE-FSL-S-1419 | 20/04/25 | 14 | UNICEF | FSTP-14-03 | C-14-D-D3-FSM-03 | D | D-3 | ABR | 50 | 21.1658 | 92.1439 | Effluent | 8.55 | 30 | 616 | 11.4 | 82 | 170 | 550 | 20500 | 58600 | 550 | 2.65% | 200 | 2480
152 | BRAC | DPHE-FSL-S-1420 | 20/04/25 | 14 | UNICEF | FSTP-14-01 | C-14-A-A4-FSM-04 | A | A-4 | ABR | 50 | 21.1517 | 92.5315 | Effluent | 8.29 | 30.9 | 926 | 20 | 55.8 | 145 | 866 | 4000 | 9600 | 550 | 1.21% | 160 | 2310
153 | BRAC | DPHE-FSL-S-1421 | 20/04/25 | 14 | UNICEF | FSTP-14-05 | C-14-E-E1-FSM-01 | E | E-1 | ABR | 50 | 21.1664 | 92.1407 | Effluent | 8.53 | 27.7 | 240 | 5.97 | 9.22 | 80 | 155 | 800 | 19000 | 20 | 0.65% | 160 | 510
154 | BRAC | DPHE-FSL-S-1422 | 20/04/25 | 14 | UNICEF | FSTP-14-07 | C-14-C-C2-FSM-05 | C | C-2 | ABR | 55 | 21.1705 | 92.1472 | Effluent | 6.89 | 28 | 145 | 45.9 | 10.82 | 42 | 170 | 10800 | 20600 | 40 | 0.82% | 120 | 1090